VIKING VSH1230

ENGINEERING SPECIFICATIONS

Clean Agent Fire Extinguishing utilizing 3M™ Novec™ 1230 Fire Protection Fluid at 360 psi with the                NFS-320 Intelligent Addressable Fire Alarm System

SECTION 1 – GENERAL SPECIFICATIONS

- SCOPE

This specification outlines the requirements for a “Total Flooding” clean agent fire extinguishing

system utilizing Viking VSH1230 with 3M™ Novec™ 1230 fluid at 360 psi utilizing an NFS-320 Intelligent Addressable Fire Alarm System. The work described in this specification includes all engineering, labor, materials, equipment and services required to install and test the clean agent fire extinguishing and control system. Contractor is to review all drawings so that the items affecting the operation of the Viking VSH1230 fire suppression system such as equipment location, air diffusers, damper closures, are considered in the design of the engineered system.

- APPLICABLE STANDARDS AND PUBLICATIONS

The design, equipment, installation, testing and maintenance of the Viking Clean Agent suppression System shall be in accordance with the applicable requirements set forth in the latest edition of the following codes and standards.

- NFPA 2001 - Clean Agent Fire Extinguishing Systems.

- NFPA 70 - National Electric Code.

- NFPA 72 – National Fire Alarm and Signaling Code.

- FM - Factory Mutual Approval Guide.

- UL - Fire Protection Equipment Directory.

- Department of Transportation (DOT) Title 49 Code of Federal Regulations

- NEMA – Enclosures for Industrial Controls and Systems.

- All Requirements of Authority Having Jurisdiction (AHJ)

The standards listed, as well as all other applicable codes, standards, and good engineering practices shall be used as "minimum" design standards.

- REQUIREMENTS

The Suppression System installation shall be made in accordance with the drawings, specifications and applicable standards. All Equipment and devices used shall be listed in the UL Fire Equipment Directory.  Should a conflict occur between the drawings and specifications, the specifications shall prevail.

- EXCLUSIONS

The work listed below shall be provided by others, or under other sections of this specification:

  - 120 VAC or 220 VAC power supply to the system control panel.

  - Interlock wiring and conduit for shutdown of HVAC, dampers and/or electric power supplies, relays or shunt trip breakers.

  - Connection to local/remote fire alarm systems or listed central alarm station(s).

- QUALITY ASSURANCE

- MANUFACTURER

- The manufacturer of the suppression system hardware and detection components shall be Viking Corporation.  (No Substitution Allowed)

- The name of the manufacturer Viking shall appear on all major components.

- All devices, components and equipment shall be the products of the same manufacturer.

- All devices, components and equipment shall be new, standard products of the manufacturer’s latest design and suitable to perform the functions intended.

- All devices and equipment shall be UL Listed and/or FM Approved.

- INSTALLER

- The installing contractor shall be trained by the supplier to design, install, test and maintain fire suppression systems.

- When possible, the installing contractor shall employ a NICET certified special hazard designer, Level III or above, who will be responsible for this project.

- The installing contractor shall be an experienced firm regularly engaged in the installation of automatic Clean Agent, or similar, fire suppression systems in strict accordance with all applicable codes and standards.

- The installing contractor must have a minimum of five (5) years experience in the design, installation and testing of Clean Agent, or similar, fire suppression systems. A list of systems of a similar nature and scope shall be provided on request.

- The installing contractor shall show evidence that his company carries a minimum $2,000,000.00 liability and completed operations insurance policy. These limits shall supersede limits required in the general conditions of the specifications.

- The installing contractor shall maintain, or have access to, a Clean Agent recharging station. The installing contractor shall provide proof of this ability to recharge the largest Clean Agent system within 24 hours after a discharge including the amount of bulk agent storage available.

- The installing contractor shall be an authorized stocking distributor of the Clean Agent system equipment so that immediate replacement parts are available from inventory.

- The installing contractor shall show proof of emergency service available on a twenty-four-hour-a-day, seven-day-a-week basis.

- SUBMITTALS

  - The installing contractor shall submit the following design information and drawings for approval prior to starting installation on this project.

- Working plans indicating detailed layout of system, locating each component (e.g. agent cylinder, control panel, electric/manual pull station, audible and visual alarms). Include control diagrams, wiring diagrams, and written sequence of operation or cause to affect matrix along with battery calculations, and pipe locations including size and length. Refer to NFPA 2001.

- Product data for each piece of equipment comprising the system including storage cylinders, control valves and pilot controls, control panels, nozzles, manual stations, detectors, alarm bells or horns, switches, and annunciators.

- Design calculations shall be derived using Viking Tools for Revit, Clean Agent Assistant or VSH “DesignManager” both have been verified by Underwriters Laboratories and Factory Mutual. Analysis shall include calculations to verify system pipe pressures, nozzle flow rates, orifice code number, piping pressure losses, component flow data, and pipe sizes considering actual and equivalent lengths of pipe and elevation changes. Designers using this software shall be trained by Viking Corporation. The software shall allow for up to 85% of the agent to be in the pipe distribution network.

d.    Manufacturer's installation and operation manual.

e.  When incorporating Viking products into a Revit Project Model - Viking Revit Families     Should be used to ensure accuracy of physical geometry and product specifications.  Viking Revit Family Models are available directly from our website.  www.vikingcorp.com

f.   To ensure accurate dimensions, Viking pipe routing tables and fittings should be used in the Revit model which are available through Viking Tools for Revit.

2)	Submit drawings, calculations and system component data sheets for approval to the local fire prevention agency, owner’s insurance underwriter, and all other authorities having jurisdiction before starting installation. Submit approved plans to the architect/engineer for record.

SECTION 2 – SYSTEM REQUIREMENTS

- SYSTEM DESCRIPTION AND OPERATION

  - The fire protection system shall be a Viking VSH1230 Total Flooding System utilizing Novec 1230 fluid at 360 psi. System is a fixed installation where equipment is designed and installed to provide fire extinguishing capability for hazards described. The system shall be supplied by Viking Corporation. (No Exceptions) Viking Corporation (480) 553-5670

- The system shall provide a minimum agent design concentration of 4.5% by volume for Class A hazards and a minimum of 5.9% by volume for Class B hazards, in all areas and/or protected spaces, at the minimum anticipated temperature within the protected area. The system should be designed to discharge its liquid contents in 10 seconds or less. System design shall not exceed 10% for normally occupied spaces, adjusted for maximum space temperature anticipated, with provisions for room evacuation before agent release. Concentration may vary depending on the AHJ but may never be less than 4.5% for Class A and Class C and may never be less than 5.9% for Class B.

- The system shall be complete in all ways. It shall include all mechanical and electrical installation, all detection and control equipment, agent storage cylinders, Novec™ 1230 fluid, discharge nozzles, pipe and fittings, manual release and abort stations, audible and visual alarm devices, auxiliary devices and controls, shutdowns, alarm interface, caution/advisory signs, functional checkout and testing, training and all other operations necessary for a functional, UL Listed and/or FM Approved Clean Agent Suppression System for use with Novec 1230 fluid.

- The system(s) shall be actuated by a combination of ionization and/or photoelectric detectors installed for maximum area coverage of 250 sq. ft. (23.2 m2) per detector, in both the room, and above ceiling protected spaces. Photoelectric detectors shall be installed in subfloor protected spaces. If the airflow is one air change per minute, photoelectric detectors only shall be installed for maximum area coverage of 125 sq. ft. (11.6 m2) per detector. (Ref. NFPA 72 & FSSA Detection & Control Guide).

- Detectors shall be Cross-Zoned detection requiring two detectors to be in alarm before release.

- Automatic operation of each protected area shall be as follows:

      - Actuation of one (1) smoke detector, within the system, shall:

  - Energize a lamp on the activated detector, display detector location on control panel and annunciator. A remote annunciator shall be provided as indicated on drawings. Annunciator shall be the FDU-80G, LCD-80 or LCD2-80. (optional)

  - Display “DETECTOR #” on the control panel LCD.

c.    Energize an alarm AGENT horn device in a coded fashion 1 second on 1 second off

for first stage.

d.   Transfer modules or auxiliary contacts which can perform auxiliary system functions

such as:

    - Operate door holder/closures on access doors

    - Transmit a signal to a fire alarm system

    - Shutdown HVAC equipment

2)     Actuation of a 2nd smoke detector, within the system, shall:

- Energize a lamp on the activated detector, display detector location on control panel and annunciator.

- Flash the PRE-DISCHARGE lamp on the control panel face.

c.   Energize a pre-discharge AGENT horn device in a coded fashion 1/2 second on 1/2

second off for 2nd stage alarm and activate strobe device in hazard.

d.   Shut down the HVAC system and/or dampers.

e.   Start time-delay sequence (not to exceed 60 seconds)

f.   System abort sequence is enabled at this time.

- After completion of the time-delay sequence, the Clean Agent system shall dis-charge and the following shall occur:

    - Appropriate cylinder(s) electric actuator shall activate. Display location on control panel and annunciator.

    - Illuminate the “DISCHARGE” lamp on the control panel face.

    - Shutdown of all power to equipment as needed.

    - Energize an AGENT strobe visual indicator(s) outside the hazard in which the discharge

has occurred.

    - Energize an “AGENT” horn device. The audio tone shall go steady.

      - The system shall be capable of being actuated by manual discharge devices located at each hazard exit. Operation of a manual device shall duplicate the sequence description above, except that the time delay and abort functions shall be bypassed. The manual discharge station shall be of the electrical actuation type and shall be supervised at the main control panel.

- Abort stations shall be provided at each exit of the protected area and shall, when operated, shall interrupt the discharge of Novec 1230 agent. The abort stations shall be momentary contacts (dead-man) requiring constant pressure to maintain contact closure.

- MATERIALS AND EQUIPMENT

A.	GENERAL REQUIREMENTS

1)	The VSH1230 Clean Agent System materials and equipment shall be standard products of the supplier’s latest design and suitable to perform the functions intended. When one or more pieces of equipment must perform the same function(s), they shall be duplicates produced by one manufacturer.

2)	All devices and equipment shall be UL Listed and/or FM approved.

3)	The fire suppression agent shall be Novec 1230 fire protection fluid; clean dry, non-corrosive, non-damaging, non-deteriorating, and meeting the requirements of NFPA 2001. The agent shall be suitable for use in normally occupied spaces. Agent shall be listed as “Acceptable” on the EPA’s SNAP list.

B.	CLEAN AGENT STORAGE AND DISTRIBUTION

1)	Each system shall have its own supply of clean agent.

2)	The system design can be modular, central storage, or a combination of both design criteria.

3)	Systems shall be designed in accordance with the manufacturer’s guidelines.

4)	Each supply shall be located within the hazard area, or as near as possible to reduce the amount of pipe and fittings required to install the system.

5)	The clean agent shall be stored in Viking Agent Storage Cylinder Assemblies. Cylinders shall be super-pressurized with dry nitrogen to an operating pressure of 360 psi @ 70°F (24.8 bar @ 20°C). Cylinders shall be of high-strength low alloy steel construction and conform to NFPA 2001.

6)	Cylinders shall have a threaded protection ring on the tank collar and ¼” steel protection cap for handling and shipment.

7)   Valve shall be constructed of forged brass and operate by means of pressure differential.

Valve shall be constructed as to not require rebuild after discharge, Valve shall allow for

means to pressurize cylinder without need for valve operation.

8)   The primary cylinder assembly(s) shall be actuated by a resettable electric actuator or by

pneumatic means from a PAE pilot cylinder. Non re-settable or explosive devices shall not be

permitted.

a. All solenoids shall be supervised by a Solenoid Monitor Switch. Viking part number

922290D & 922291D

9)	The cylinders shall be mounted using wall racks on solid walls. The cylinders and racks shall be arranged to allow a service aisle for cylinder removal and cylinder weighing.

10)	Each cylinder assembly shall have a contact pressure gauge with integrated low pressure switch to provide visual and electrical supervision of the cylinder pressure. The low pressure switch shall be wired to the control panel to provide an audible and visual supervisory condition signal in the event the cylinder pressure drops below 10% working pressure. The pressure gauge shall be color coded to provide an easy, visual indication of cylinder pressure.

11)	Each cylinder assembly shall have a pressure relief provision that automatically operates before the internal pressure exceeds 710 psi (49 bar).

12)	When more than one cylinder is connected to a common manifold, a check valve with adaptor shall be provided with each cylinder.

13)	Engineered discharge nozzles shall be provided within the manufacturer’s guidelines to distribute the Novec™ 1230 fluid throughout the protected spaces. The nozzles shall be designed to provide proper agent quantity and distribution. Nozzles shall be available in ½ in. through 2 in. pipe sizes. Each size shall be available in 180°and 360 º distribution patterns.

a.	Nozzles shall be permanently marked as to part number and orifice diameter.

b.	Nozzles shall be of the type utilizing internal orifice plates.

c.	Nozzles should be approved to be used in the upright or pendant position.

d.   Ceiling plates, can be used with the nozzles to conceal pipe entry holes through ceiling

tiles

e    180° Nozzles shall have 35.77 ft. radius of coverage

f.    Back to back 180° nozzles shall be approved for installation

g.   Nozzle flow rate shall be capable of 386 pounds

h.   System vertical tank to nozzle height shall be capable of 53.8’ feet

If nozzles are only located above the tank outlet, then the maximum elevation difference	                    between the tank and outlet and the furthest horizontal pipe run or discharge nozzle

(whichever is furthest) shall not exceed 53.8 ft.

If nozzles are only located below the tank outlet, then the maximum elevation difference

between the tank and outlet and the furthest horizontal pipe run or discharge nozzle

(whichever is furthest) shall not exceed 53.8 ft.

If nozzles are only located above and below the tank outlet, then the maximum

elevation difference between discharge nozzles shall not exceed 53.8 ft.

14)	Distribution piping, and fittings, shall be installed in accordance with the manufacturer’s requirements, NFPA 2001 and approved piping standards and guidelines. All distribution piping shall be installed by qualified individuals using accepted practices and quality procedures. All piping shall be adequately supported and anchored at all directional changes and nozzle locations. The piping shall be laid out to give maximum flow and to avoid possible mechanical, chemical or other damage. Installation shall follow drawings as closely as possible. System designer must be consulted for anything other than minor deviations in pipe routing.

a.	Black or galvanized steel pipe shall be either ASTM A53 seamless or electric welded, Grade A or B or ASTM A-106, Grade A, B, or C. ASTM A-120, ordinary cast-iron pipe, aluminum pipe, or non-metallic pipe shall not be used. Stainless steel pipe shall be 304, 316, 304L, or 316L for threaded connections or 304L or 316L for welded connections.

b.	Threaded fittings must comply with NFPA 2001 and be at a minimum class 300 malleable iron, class 300 ductile iron. Cast iron and Class 150 pound fittings shall not be used.

c.	Grooved fittings and couplings must comply with NFPA 2001. Piping shall be rolled or cut grooved in accordance with the fitting or coupling manufacturer's guidelines.

d.	Gaskets must be compatible with Novec 1230 fluid (typically EPDM having a temperature range of -30°F to 230°F [-34°C to 110°C]). Gasket lubricant must be in accordance with manufacturer's specifications.

e.	The minimum allowable working pressure at 70°F (21.1°C) for pipe and fittings in closed sections of pipe must be greater than or equal to the maximum operating pressure of the discharge pipe safety relief valve.

f.	Reductions in pipe sizes may be accomplished using threaded or grooved concentric reducing fittings, steel or stainless steel concentric swage fittings, or steel or stainless steel reducing bushings. All such fittings must comply with NFPA 2001. Pipe reductions can be made using machined or forged steel hex bushings. Malleable and/or cast iron bushings are NOT to be used.

g.	All piping shall be reamed, blown clear and swabbed with suitable solvents to remove burrs, mill varnish and cutting oils before assembly.

h.	All male threads on pipe shall be tapped with approved Teflon tape.

I.	Piping shall be pneumatically tested in a closed circuit for a period of 10 minutes at 40 psi (2.76 bar) per the latest edition of NFPA 2001. At the end of 10 minutes, the pressure drop shall not exceed 20 percent of the test pressure. The pressure test shall be permitted to be omitted if the total piping contains no more than one change in direction fitting between the storage container and the discharge nozzle, and where all piping is physically tested for tightness.

C.	CONTROL PANEL

1)	The control panel shall be a NFS-320 Intelligent Addressable Fire Alarm System and its components shall be UL Listed and/or FM Approved for release.

2)	The NFS-320 Intelligent Addressable Fire Alarm System shall perform all functions necessary to operate the system detection, actuation, notification and auxiliary functions as outlined.

3)	The NFS-320 Intelligent Addressable Fire Alarm System shall be capable of providing 8.0 AH or 12.0 AH battery standby power supplies, providing from 24 to 90 hours standby.

4)	The NFS-320 Intelligent Addressable Fire Alarm System shall support Cross-Zoned, Single Detector Release and Manual Release detection/actuation methods.

5)		The NFS-320 Intelligent Addressable Fire Alarm System shall provide the following capabilities and functions:

  - The system shall include one isolated intelligent Signaling Line Circuit (SLC), Style 4, 6, or 7

  - Up to 159 detectors and 159 modules 318 devices maximum

  - A 6 .0 A power supply with four Class A/B built in Notification Appliance Circuits (NAC). selectable System Sensor, Wheelock, or Gentex strobe synchronization

  - Standard 80 character display LCD

  - Built in Alarm, Trouble, Security, and Supervisory relays

  - Certified for seismic applications when used with the appropriate seismic mounting kit

  - NOTIFIER VeriFire® Tools online or offline programming utility. Upload/Download, save, store, check, compare, and simulate panel databases. Upgrade panel firmware

  - Auto programming and Walk Test reports

  - Optional universal 318-point DACT

  - 80 character remote annunciator (up to 32)

  - EIA-485 annunciator, including custom graphics

  - Printer interface (80-column and 40-column printers).

  - History file with 800-event capacity in nonvolatile memory, plus separate 200-event Alarm only file

  - Alarm Verification selection per point, with tally

  - Pre-signal/Positive Alarm Sequence (PAS)

  - Silence inhibit and Auto Silence timer options

  - NAC coding functions: March time, Temporal, California two-stage coding, Canadian     two-stage

  - Strobe synchronization

  - Field-programmable on panel or on PC, with NOTIFIER VeriFire® Tools program check, compare, simulate

  - Full QWERTY keypad

  - Battery charger supports 18 – 200 AH batteries

  - Non-alarm points for lower priority functions

  - Remote ACK/Signal Silence/System Reset/Drill via monitor modules.

- ANNUNCIATOR

  - Annunciator shall be the FDU-80G, LCD-80 or LCD2-80. (optional)

E.	DETECTORS

- The detectors shall be spaced and installed in accordance with the manufacturer’s specifications and the guidelines of NFPA 72.

- The detectors shall use the photoelectric (light-scattering) principle to measure smoke density and shall, on command from the control panel, send data to the panel representing the analog level of smoke density. Photoelectric Smoke Detector shall be Addressable FSP-851.  Viking P/N 16646

- The detectors shall use the dual-chamber ionization principle to measure products of combustion and shall, on command from the control panel, send data to the panel representing the analog level of products of combustion. Ionization Smoke Detector shall be Addressable FSI-851.  Viking P/N 16909

- Addressable-analog communication.

- Two-wire SLC connection.

- Remote test feature from the panel.

- Built-in functional test switch activated by external magnet.

- Built-in tamper-resistant feature.

- Optional relay, isolator, and sounder bases.

F.	MANUAL RELEASE (ELECTRIC)

- The electric manual release station shall be a dual action device which provides a means of manually discharging the clean agent fire extinguishing system when used in conjunction with the NFS-320 Intelligent Addressable Fire Alarm System.

- The manual release station shall be addressable Viking P/N 16653, or double action manual releasing stations shall be addressable using FMM-101 monitor module.  .

- The manual release station shall be a dual action device requiring two distinct operations to initiate a system actuation. Stations shall be suitable for surface mounting or semi-flush mounting as shown on the plans, and shall be installed not less than 42 in. (1.1 m), and not more than 48 in. (1.2 m) above the finished floor

- The manual release station shall bypass the time delay and abort functions, shall cause the system to discharge and shall cause all release and shutdown devices to operate in the same manner as if the system had operated automatically.

- A manual release station shall be located at each exit from the protected hazard.

G.	MANUAL RELEASE (MECHANICAL)

- Mechanical Manual Release shall be made available in the event all battery back-up and commercial power is lost. Viking P/N 887668 Manual Release shall be installed atop the electric actuator. Consideration should be given for convenience of operation and egress from the hazard area(s).

H.	 ABORT STATION

- The optional Abort Station shall be “Dead Man” type and shall be located next to each manual release station.

- “Locking” or “Keyed” abort stations shall not be permitted. Stations shall be suitable for surface mounting or semi-flush mounting as shown on the plans, and shall be installed not less than 42 in. (1.1 m), and not more than 48 in. (1.2 m) above the finished floor.

- The Abort Station shall be Viking P/N 17120.  Abort station shall be addressable using FMM-101 monitor module.

I.	AUDIBLE AND VISUAL ALARMS

- Audible alarm and visual signal devices shall operate from the NFS-320 Intelligent Addressable Fire Alarm System.

- Alarms shall be UL Listed or FM Approved and operate on 24 VDC nominal.

- Audible alarms shall provide continuous or interrupted tones with an output sound level of at least 90 dba measured at 10 feet from the device.  The appliance shall be placed 80 in. (2.0 m) above the highest floor level within the space, or 6 in. (15.2 cm) below the ceiling, whichever is lower.

- A Strobe device shall be placed outside, and above, each exit door

- Alarm bell shall be UL Listed or FM Approved and operate on 24 VDC nominal.

- The appliance shall be placed 80 in. (2.0 m) above the highest floor level within the space, or 6in. (15.2 cm) below the ceiling or whichever is lower.

J.   MODULES

- FMM-1 is a standard-sized module (typically mounts to a 4" [10.16 cm] square box) that supervises either a Style D (Class or Style B (Class B) circuit of dry-contact input devices.

- FMM-101 is a miniature monitor module a mere 1.3" (3.302 cm) H x 2.75" (6.985 cm) W x 0.5" (1.270 cm) D that supervises a Style B (Class B) circuit of dry-contact input devices. Its compact design allows the FMM-101(A) to be mounted in a single-gang box behind the device it monitors.

- FZM-1 is a standard-sized module that monitors and supervises compatible two-wire, 24 volt, smoke detectors on a Style D (Class A) or Style B (Class B) circuit.

- FDM-1 is a standard-sized dual monitor module that monitors and supervises two independent two-wire Style B (Class dry-contact initiating device circuits (IDCs) at two separate, consecutive addresses in intelligent, two wire systems.

- ISO-X Isolator modules shall be provided to automatically isolate wire-to-wire short circuits                                                         on a Signaling Line Circuit (SLC) loop. The isolator module shall limit the number of          modules or detectors that may be rendered inoperative by a short circuit fault on the SLC Loop. At least one isolator module shall be provided for each protected zone of the building.

- FCM-1 Addressable Control Module provides intelligent fire alarm control panels a circuit for Notification Appliances (horns, strobes, speakers, etc.). Addressability allows the FCM-1(A) to be activated, either manually or through panel programming, on a select (zone or area of coverage) basis.

- FRM-1 Addressable Relay Module provides the system with a dry-contact output for activating a variety of auxiliary devices, such as fans, dampers, control equipment, etc. Addressability allows the dry contact to be activated, either manually or through panel programming, on a select basis.

- FCM-1-REL Releasing Control Module is specifically designed for fire suppression releasing applications in Flash-Scan® systems. Power to the release agent solenoid(s) runs through the module for full-time monitoring and supervision.

K.   BATTERIES

1)	Shall be 12.0 volt, Gell-Cell type (2 required).

2)	Battery shall have sufficient capacity to power the fire alarm system for not less than twenty-four hours plus 5 minutes of alarm upon a normal AC power failure. Optional battery power for ninety hours

3)	The batteries are to be completely maintenance free.

L.    ELECTRICAL INSTALLATION

1)	Installation shall be in accordance with the NFPA 70 (NEC), NFPA 72, NFPA 2001, local and state codes, as shown on the drawings, and as recommended by the major equipment manufacturer.

2)	All conduit, junction boxes, conduit supports and hangers shall be concealed in finished areas and may be exposed in unfinished areas. Conduit installation shall be in accordance with The National Electrical Code (NEC), local and state requirements. Smoke detectors shall not be installed prior to the system programming and test period. If construction is ongoing during this period, measures shall be taken to protect smoke detectors from contamination and physical damage.

3)	All fire detection and alarm system devices, control panels and remote annunciators shall be flush mounted when located in finished areas and may be surface mounted when located in unfinished areas.

SECTION 3 – DOCUMENTATION AND TESTING

- SYSTEM INSPECTION AND CHECKOUT

After the system installation has been completed, the entire system shall be checked out, inspected and functionally tested by qualified, trained personnel, in accordance with the manufacturer’s recommended procedures and NFPA standards.

A.	All containers and distribution piping shall be checked for proper mounting and installation.

B.	All electrical wiring shall be tested for proper connection, continuity and resistance to earth.

C.	The complete system shall be functionally tested, in the presence of the owner or his representative, and all functions, including system and equipment interlocks, must be operational at least five (5) days prior to the final acceptance tests.

1)	Each detector shall be tested in accordance with the manufacturer’s recommended procedures, and test values recorded.

2)	All system and equipment interlocks, such as door release devices, audible and visual devices, equipment shutdowns, local and remote alarms, etc. shall function as required and designed.

3)	Each control panel circuit shall be tested for trouble by inducing a trouble condition into the system.

- TRAINING REQUIREMENTS

Prior to final acceptance, the installing contractor shall provide operational training to each shift of the owner’s personnel. Each training session shall include control panel operation, manual and (optional) abort functions, trouble procedures, supervisory procedures, auxiliary functions and emergency procedures.

- OPERATION AND MAINTENANCE

Prior to final acceptance, the installing contractor shall provide complete operation and maintenance instruction manuals, four (4) copies for each system, to the owner. All aspects of system operation and maintenance shall be detailed, including piping isometrics, wiring diagrams of all circuits, a written description of the system design, sequence of operation and drawing(s) illustrating control logic and equipment used in the system. Checklists and procedures for emergency situations, troubleshooting techniques, maintenance operations and procedures shall be included in the manual.

- AS-BUILT DRAWINGS

Upon completion of each system, the installing contractor shall provide four (4) copies of system “As-Built” drawings to the owner. The drawings shall show actual installation details including all equipment locations (e.g. control panel(s), agent container(s), detectors, alarms, manuals and aborts, etc.) as well as piping and conduit routing details. Show all room or facilities modifications, including door and/or damper installations completed.

- ACCEPTANCE TESTS

A.	At the time “As-Built” drawings and maintenance/operations manuals are submitted, the installing contractor shall submit a “Test Plan” describing procedures to be used to test the control system(s). The Test Plan shall include a step-by-step description of all tests to be performed and shall indicate the type and location of test apparatus to be employed. The tests shall demonstrate that the operational and installation requirements of this specification have been met. All tests shall be conducted in the presence of the owner and shall not be conducted until the Test Plan has been approved.

B.	The tests shall demonstrate that the entire control system functions as designed and intended. All circuits shall be tested: automatic actuation, solenoid and manual actuation, HVAC and power shutdowns, audible and visual alarm devices and manual override of abort functions. Supervision of all panel circuits, including AC power and battery power supplies, shall be tested and qualified.

C.	A room pressurization test shall be conducted, in each protected space, to determine the presence of openings which would affect the agent concentration levels. The test(s) shall be conducted using the Door Fan system with integrated computer program. All testing shall be in accordance with NFPA 2001.

D.	If room pressurization testing indicates that openings exist which would result in leakage and/or loss of the extinguishing agent, the installing contractor shall be responsible for coordinating the proper sealing of the protected space(s) by the general contractor or his sub-contractor or agent. The general contractor shall be responsible for adequately sealing all protected space(s) against agent loss or leakage. The installing contractor shall inspect all work to ascertain that the protected space(s) have been adequately and properly sealed. THE SUPPRESSION SYSTEM INSTALLING CONTRACTOR SHALL BE RESPONSIBLE FOR THE SUCCESS OF THE ROOM PRESSURIZATION TESTS. If the first room pressurization test is not successful, in accordance with these specifications, the installing contractor shall direct the general contractor to determine, and correct, the cause of the test failure. Copies of successful test results shall be submitted to the owner for record. Upon acceptance by the owner, the completed system(s) shall be placed into service.

- SYSTEM INSPECTIONS

A.	The installing contractor shall provide two (2) inspections of each system, installed under this contract, during the one-year warranty period. The first inspection shall be at the six-month interval, and the second inspection at the 12-month interval, after system acceptance. Inspections shall be conducted in accordance with the manufacturer’s guidelines and the recommendations of NFPA 2001.

B.	Documents certifying satisfactory system(s) operation shall be submitted to the owner upon completion of each inspection.

- WARRANTY

All Viking components furnished and installed under this contract shall be warranted against defects in design, materials and workmanship for the full warranty period which is standard with the manufacturer, but in no case less than one (1) year from the date of system acceptance.