VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Non Interlocked) Electric Detection Method

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be released by either an activation of the supplemental electric detection system or the activation of a sprinkler head on the system.  The preaction system riser shall be of a listed and approved assembly.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-line Check Valve.

N/C Solenoid Valve

The deluge valve priming water release device shall be an electrically operated Normally Closed solenoid valve.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves and Viking Model H or J Flow Control Valves.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

- Electric fixed temperature self-restoring releases.  (Insert applicable product specification.)

- Electric smoke detection devices.  Smoke detection devices to be compatible with system control panel.  (Insert applicable product specification.)

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The low air pressure supervisory switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials and accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Non Interlocked) Pneumatic Detection Method

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be released by either an activation of the supplemental pneumatic detection system or the activation of a sprinkler head on the system.  The preaction system riser shall be of a listed and approved assembly.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-line Check Valve.

Pneumatic Actuator

The preaction or deluge systems utilizing pneumatic release detectors shall employ a pneumatic actuator between the detection and the operating systems.  The device shall actuate a release in the deluge valve priming water supply.  The actuator of the pneumatic release system shall be UL Listed and Factory Mutual Approved for use with the deluge valve installed.  The Pneumatic Actuator manufacturer to be The Viking Corporation.  Pneumatic Actuator to be Viking Model H-1.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

Sprinklers

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikingcorp.com

2. 	Substitutions: Not permitted.

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

- Pneumatic rate-of-rise compensating vent type detector with a fixed temperature release.  (Insert applicable product specification.)

- Pneumatic fixed temperature pilot operated release line.  (Insert applicable product specification.)

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The low air pressure supervisory switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12 volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking Model VFR400 Multi-Hazard Release Control Panel.

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials and accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Non Interlocked) Hydraulic Detection Method

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be released by either an activation of the supplemental Hydraulic detection system or the activation of a sprinkler head on the system.  The preaction system riser shall be of a listed and approved assembly.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-line Check Valve.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

A.	Hydraulic rate-of-rise compensating vent type detector with a fixed temperature release.  (Insert applicable product specification.)

B.	Hydraulic fixed temperature pilot operated release line.  (Insert applicable product specification.)

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The low air pressure supervisory switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials and accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Single Interlocked) Electric Detection Methods

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by activation of the supplemental electric detection system only.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the most current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of the Single Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve..

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

Normally Closed Solenoid Valve

The deluge valve priming water release device shall be an electrically operated Normally Closed solenoid valve when electric releases are used as the supplemental detection system.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves and Viking Model H or J Flow Control Valves.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking Model VFR400 Multi-Hazard Release Control Panel.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

A.	Electric fixed temperature self-restoring releases.  (Insert applicable product specification.)

B.	Electric smoke detection devices.  Smoke detection devices to be compatible with system control panel.  (Insert applicable product specification.)

C.	Other compatible listed electrical detectors.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be

compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual

Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm

Pressure Switch shall be Potter, model number PS101A or PS102A.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials and accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Single Interlocked) Pneumatic Detection Methods

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by activation of the supplemental pneumatic detection system only.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the most current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of the Single Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

Pneumatic Actuator

Preaction or deluge systems utilizing pneumatic release detectors shall employ a pneumatic actuator between the detection and the operating systems.  The device shall actuate a release in the deluge valve priming water supply.  The actuator of the pneumatic release system shall be UL Listed and Factory Mutual Approved for use with the deluge valve installed.  The Pneumatic Actuator manufacturer to be The Viking Corporation.  Pneumatic Actuator to be Viking Model H-1.

Sprinklers

MANUFACTURERS

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

A.	Pneumatic rate-of-rise compensating vent type detector with a fixed temperature release.  (Insert applicable product specification.)

B.	Pneumatic fixed temperature pilot operated release line.  (Insert applicable product specification.)

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking Model VFR400 Multi-Hazard Release Control Panel.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials and accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Single Interlocked) Hydraulic Detection Methods

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by activation of the supplemental Hydraulic detection system only.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the most current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of the Single Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

A.	Hydraulic rate-of-rise compensating vent type detector with a fixed temperature release.  (Insert applicable product specification.)

B.	Hydraulic fixed temperature pilot operated release line.  (Insert applicable product specification.)

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve..

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking Model VFR400 Multi-Hazard Release Control Panel.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials and accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Trimpac® Preaction System (Single Interlocked) Pneumatic Release

A Viking Trimpac Single Interlock Pneumatic Release Preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be released by an activation of the pneumatic release system only.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the most current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of the Single Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Viking Trimpac® Single Interlock Pneumatic Release

The deluge valve trim shall be a trim package for a deluge valve with a specific release device and release module for the desired application manufactured and tested in a metal enclosure.  The metal enclosure shall be 16-gauge steel painted with a red epoxy powder coat.  The standard trim normally required on a deluge valve will be enclosed in this single cabinet.  The Trimpac shall provide access doors for the emergency release and alarm test valve for manual operation of these trim valves.  The Trimpac shall be equipped with priming water pressure and water supply gauge view-ports for easy monitoring of water pressures.  The enclosure shall be designed to protect the trim valves from inadvertent operation.  The system shall be piped (or use the stainless steel hose package) from the valve body to the enclosure assembly.  The Trimpac Model B-4 can be utilized for pneumatic release single interlocked preaction systems with the Viking Model E-1 or F-1 Deluge Valves in all sizes.  The unit shall be rated for 250 PSI (1724 kPa).  The Deluge Valve Trim shall be Viking Trimpac Single Interlock Pneumatic Release Model B-4, part number 13793B-4.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

Pneumatic Actuator

Preaction or deluge systems utilizing pneumatic release detectors shall employ a pneumatic actuator between the detection and the operating systems.  The device shall actuate a release in the deluge valve priming water supply.  The actuator of the pneumatic release system shall be UL Listed and Factory Mutual Approved for use with the deluge valve installed.  The Pneumatic Actuator manufacturer to be The Viking Corporation.  Pneumatic Actuator to be Viking Model H-1.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100

PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Supplemental Detection System

A supplemental detection system shall be provided for the preaction systems.  Acceptable supplemental detection devices are:

A.	Pneumatic rate-of-rise compensating vent type detector with a fixed temperature release.  (Insert applicable product specification.)

B.	Pneumatic fixed temperature pilot operated release line.  (Insert applicable product specification.)

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials or accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Trimpac® Preaction System (Single Interlocked) Electric Release

A Viking Trimpac Single Interlock Electric Release Preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be released by an electric solenoid valve.  The electric solenoid valve will release the prime water only upon activation of the supplemental detection system.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of a Single Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Viking Trimpac® Single Interlock Electric Release

The deluge valve trim shall be a trim package for a deluge valve with a specific release device and release module for the desired application manufactured and tested in a metal enclosure.  The metal enclosure shall be 16-gauge steel painted with a red epoxy powder coat.  The standard trim normally required on a deluge valve will be enclosed in this single cabinet.  The Trimpac shall provide access doors for the emergency release and alarm test valve for manual operation of these trim valves.  The Trimpac shall be equipped with priming water pressure and water supply gauge view-ports for easy monitoring of water pressures.  The enclosure shall be designed to protect the trim valves from inadvertent operation.  The system shall be piped (or use the stainless steel hose package) from the valve body to the enclosure assembly.  The Trimpac Model B-3 can be utilized for electric release single interlocked preaction systems with the Viking Model E-1 or F-1 Deluge Valves in all sizes.  The unit shall be rated for 250 PSI (1724 kPa).  The Deluge Valve Trim shall be Viking Trimpac Single Interlock Electric Release Model B-3, part number 13792B-3.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

Detection

The release system shall incorporate as part of the operation of the system, electrical detection system.

A.	Electric fixed temperature self-restoring releases.  (Insert applicable product specification.)

B.	Electric smoke detection devices.  Smoke detection devices to be compatible with system control panel.  (Insert applicable product specification.)

C.	Other compatible listed electrical detectors.

Release Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking Model VFR400 Multi-Hazard Release Control Panel.

Normally Closed Solenoid Valve

The deluge valve priming water release device shall be an electrically operated solenoid valve.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves and Viking Model H or J Flow Control Valves.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the system riser.

D.	A riser mounted air compressor listed as an air maintenance compressor.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100

PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary

alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials or accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Single Interlocked) Electric Release Cross-Zone

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be released by an electric solenoid valve.  The electric solenoid valve will release the prime water only upon activation of both zones of the supplemental detection system.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of a Single Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved or grooved by grooved, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

Detection

The release system shall incorporate as part of the operation of the system, a cross-zone detection system.

A.	Electric fixed temperature self-restoring releases.  (Insert applicable product specification.)

B.	Electric smoke detection devices.  Smoke detection devices to be compatible with system control panel.  (Insert applicable product specification.)

C.	Other compatible listed electrical detectors.

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Solenoid Valve

The deluge valve priming water release device shall be an electrically operated solenoid valve.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves and Viking Model H or J Flow Control Valves.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the system riser.

D.	A riser mounted air compressor listed as an air maintenance compressor.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100

PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials or accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Double Interlocked) Pneumatic/Pneumatic Release

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by a pneumatic supplemental detection device and valve system piping charged with compressed air.  Pneumatic actuators in series in the release line assigned to the pneumatic release system and the system supervisory air pressure will open upon activation of the supplemental detection system and the activation of a sprinkler head on the system piping.  The opening of the deluge valve shall not be dependent on the order of activation of the release devices, only that both devices must activate before the deluge valve will open.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of a Double Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Supplemental Detection System:

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

A.	Pneumatic rate-of-rise compensating vent type detector with a fixed temperature release.  Preaction systems utilizing pneumatic release of the deluge valve prime water pressure shall employ a rate-of-rise release detector.  The rate-of-rise release shall activate release when a rise of temperature of 15°F over the period of one minute is experienced.  The rate-of-rise release shall have a means of installing a 155°F fixed temperature release on the device.  The rate-of-rise release shall be automatically resetting.  Device shall be UL Listed and Factory Mutual Approved.  Systems utilizing nitrogen as an air supply shall be factory tested for such application.  The Rate-of-Rise Release manufacturer to be The Viking Corporation.  Rate-of-Rise Release to be Viking Model C-1.

B.	Pneumatic fixed temperature pilot operated release line.  Preaction systems utilizing pneumatic release of the deluge valve prime water pressure shall employ a fixed temperature release device.  The fixed temperature release may be a listed fixed temperature release or listed upright sprinkler head.  The device shall be UL Listed and Factory Mutual Approved.  The Fixed Temperature Release manufacturer to be The Viking Corporation.  Fixed Temperature Release to be Viking Model M, or Model M Upright Sprinklers.

Pneumatic Actuator (Two required)

Preaction or deluge systems utilizing pneumatic release detectors shall employ a pneumatic actuator between the detection and the operating systems.  The device shall actuate a release in the deluge valve priming water supply.  The actuator of the pneumatic release system shall be UL Listed and Factory Mutual Approved for use with the deluge valve installed.  The Pneumatic Actuator manufacturer to be The Viking Corporation.  Pneumatic Actuator to be Viking Model H-1.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet and a separate air maintenance device for the supplemental detection system.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser and a separate air maintenance device for the supplemental detection device.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

D.	A riser mounted air compressor listed as an air maintenance compressor.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Quick Opening Device:

If water cannot be delivered to the dry system inspectors test connection within a minute of opening, a quick opening device shall be provided on the system riser.  The quick opening device shall be of the same manufacturer as the dry pipe valve.  The sprinkler system quick opening device shall be an accelerator with an external anti-flooding device.  Accelerator manufacturer to be The Viking Corporation.  Accelerator to be Viking Model E-1.

Model LD-1 Anti-Column Device:

The anti-column device shall have a stainless steel body and shall utilize a stainless steel float ball which rises when water in the system accumulates to the level of the anti-column device. When the float ball rises, water is automatically drained from the system. The anti-column device shall be UL listed and FM approved. The anti-column device shall be manufactured by the Viking Corporation. Anti-column Device Model to be Viking LD-1.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials or accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2. (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Trimpac® Preaction System (Double Interlocked) Electric/Pneumatic Release

A Viking Trimpac Double Interlock Electric/Pneumatic Release Preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by an electric solenoid valve and a pneumatic actuator.  Electric solenoid valve will open upon activation of the electrical supplemental detection system.  Pneumatic actuator shall open upon activation of a sprinkler head on the sprinkler system.  The opening of the deluge valve shall not be dependent on the order of activation of the release devices, only that both devices must activate before the deluge valve will open.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of a Double Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Viking Trimpac® Double Interlock Preaction Electric/Pneumatic Release

The deluge valve trim shall be a trim package for a deluge valve with a specific release device and release module for the desired application manufactured and tested in a metal enclosure.  The metal enclosure shall be 16-gauge steel painted with a red epoxy powder coat.  The standard trim normally required on a deluge valve will be enclosed in this single cabinet.  The Trimpac shall provide access doors for the emergency release and alarm test valve for manual operation of these trim valves.  The Trimpac shall be equipped with priming water pressure and water supply gauge view-ports for easy monitoring of water pressures.  The enclosure shall be designed to protect the trim valves from inadvertent operation.  The system shall be piped (or use the stainless steel hose package) from the valve body to the enclosure assembly.  The Trimpac Model B-5 can be utilized for electric/pneumatic release double interlocked preaction systems with the Viking Model E-1 or F-1 Deluge Valves in all sizes.  The unit shall be rated for 250 PSI (1724 kPa).  The Deluge Valve Trim shall be Viking Trimpac Double Interlocked Preaction Electric/Pneumatic Model B-5, part number 13794B-5.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no cases less than 175 PSI.

Detection

The release system shall incorporate as part of the operation of the system, a compatible electric detection system.  (Insert applicable detection system.)  The detection devices installed shall be compatible with the Deluge Valve Release Control Panel.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

- Electric fixed temperature self-restoring releases.  (Insert applicable product specification.)

- Electric smoke detection devices.  Smoke detection devices to be compatible with system control panel.  (Insert applicable product specification.)

Release Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Pneumatic Actuator

Preaction or deluge systems utilizing pneumatic release detectors shall employ a pneumatic actuator between the detection and the operating systems.  The device shall actuate a release in the deluge valve priming water supply.  The actuator of the pneumatic release system shall be UL Listed and Factory Mutual Approved for use with the deluge valve installed.  The Pneumatic Actuator manufacturer to be The Viking Corporation.  Pneumatic Actuator to be Viking Model H-1.

Normally Closed Solenoid Valve

The deluge valve priming water release device shall be an electrically operated solenoid valve.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves and Viking Model H or J Flow Control Valves.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the system riser.

D.	A riser mounted compressor listed as an air maintenance compressor.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Quick Opening Device:

If water cannot be delivered to the dry system inspectors test connection within a minute of opening, a quick opening device shall be provided on the system riser.  The quick opening device shall be of the same manufacturer as the dry pipe valve.  The sprinkler system quick opening device shall be an accelerator with an external anti-flooding device.  Accelerator manufacturer to be The Viking Corporation.  Accelerator to be Viking Model E-1.

Model LD-1 Anti-Column Device:

The anti-column device shall have a stainless steel body and shall utilize a stainless steel float ball which rises when water in the system accumulates to the level of the anti-column device. When the float ball rises, water is automatically drained from the system. The anti-column device shall be UL listed and FM approved. The anti-column device shall be manufactured by the Viking Corporation. Anti-column Device Model to be Viking LD-1.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials or accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Double Interlocked) Electric/Pneumatic Release

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by an electric solenoid valve and a pneumatic actuator.  Electric solenoid valve will open upon activation of the electrical supplemental detection system.  Pneumatic actuator shall open upon activation of a sprinkler head on the sprinkler system.  The opening of the deluge valve shall not be dependent on the order of activation of the release devices, only that both devices must activate before the deluge valve will open.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of a Double Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no cases less than 175 PSI.

Detection

The release system shall incorporate as part of the operation of the system, a compatible electric detection system.  (Insert applicable detection system.)  The detection devices installed shall be compatible with the Deluge Valve Release Control Panel.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

- Electric fixed temperature self-restoring releases.  (Insert applicable product specification.)

- Electric smoke detection devices.  Smoke detection devices to be compatible with system control panel.  (Insert applicable product specification.)

Release Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Normally Closed Solenoid Valve

The deluge valve priming water release device shall be an electrically operated Normally closed solenoid valve when electric releases are used as the supplemental detection system.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves.

Pneumatic Actuator

Preaction or deluge systems utilizing pneumatic release detectors shall employ a pneumatic actuator between the detection and the operating systems.  The device shall actuate a release in the deluge valve priming water supply.  The actuator of the pneumatic release system shall be UL Listed and Factory Mutual Approved for use with the deluge valve installed.  The Pneumatic Actuator manufacturer to be The Viking Corporation.  Pneumatic Actuator to be Viking Model H-1.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the system riser.

D.	A riser mounted compressor listed as an air maintenance compressor.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Quick Opening Device:

If water cannot be delivered to the dry system inspectors test connection within a minute of opening, a quick opening device shall be provided on the system riser.  The quick opening device shall be of the same manufacturer as the dry pipe valve.  The sprinkler system quick opening device shall be an accelerator with an external anti-flooding device.  Accelerator manufacturer to be The Viking Corporation.  Accelerator to be Viking Model E-1.

Model LD-1 Anti-Column Device:

The anti-column device shall have a stainless steel body and shall utilize a stainless steel float ball which rises when water in the system accumulates to the level of the anti-column device. When the float ball rises, water is automatically drained from the system. The anti-column device shall be UL listed and FM approved. The anti-column device shall be manufactured by the Viking Corporation. Anti-column Device Model to be Viking LD-1.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials or accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Trimpac® Preaction System (Double Interlocked) Electric/Pneulectric Release

A Viking Trimpac Double Interlock Electric/Pneulectric preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by an electric solenoid valve.  Electric solenoid valve will open upon activation of the electrical supplemental detection system and a low air pressure alarm caused by an opening of a sprinkler head.  The opening of the deluge valve shall not be dependent on the order of activation of the release devices, only that both devices must activate before the deluge valve will open.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of a Double Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Viking Trimpac® Double Interlock Preaction Electric/Pneu-lectric Release

The deluge valve trim shall be a trim package for a deluge valve with a specific release device and release module for the desired application manufactured and tested in a metal enclosure.  The metal enclosure shall be 16-gauge steel painted with a red epoxy powder coat.  The standard trim normally required on a deluge valve will be enclosed in this single cabinet.  The Trimpac shall provide access doors for the emergency release and alarm test valve for manual operation of these trim valves.  The Trimpac shall be equipped with priming water pressure and water supply gauge view-ports for easy monitoring of water pressures.  The enclosure shall be designed to protect the trim valves from inadvertent operation.  The system shall be piped (or use the stainless steel hose package) from the valve body to the enclosure assembly.  The Trimpac Model B-6 can be utilized for electric/pneu-lectric release double interlocked preaction systems with the Viking Model E-1 or F-1 Deluge Valves in all sizes.  The unit shall be rated for 250 PSI (1724 kPa).  The Deluge Valve Trim shall be Viking Trimpac Double Interlocked Preaction Electric/Pneu-lectric Model B-6, part number 13796B-6.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no cases less than 175 PSI.

Detection

The detection shall be of the cross-zoned type.  The electric detection system and the low air pressure alarm will be required prior to the opening of the normally closed solenoid valve, thereby, releasing the deluge valve prime pressure.  Activation of one zone of detectors (electric detector or low air supervisory switch) will cause an alarm in the zone but release will not occur until the second zone is activated.

Release Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Normally Closed Solenoid Valve

The deluge valve priming water release device shall be an electrically operated solenoid valve.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid

valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves and Viking Model H or J Flow Control Valves.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the system riser.

D.	A riser mounted compressor listed as an air maintenance compressor.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Quick Opening Device:

If water cannot be delivered to the dry system inspectors test connection within a minute of opening, a quick opening device shall be provided on the system riser.  The quick opening device shall be of the same manufacturer as the dry pipe valve.  The sprinkler system quick opening device shall be an accelerator with an external anti-flooding device.  Accelerator manufacturer to be The Viking Corporation.  Accelerator to be Viking Model E-1.

Model LD-1 Anti-Column Device:

The anti-column device shall have a stainless steel body and shall utilize a stainless steel float ball which rises when water in the system accumulates to the level of the anti-column device. When the float ball rises, water is automatically drained from the system. The anti-column device shall be UL listed and FM approved. The anti-column device shall be manufactured by the Viking Corporation. Anti-column Device Model to be Viking LD-1.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials or accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 orG-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

Preaction System (Double Interlocked) Electric/Pneulectric Release

A preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by an electric solenoid valve.  Electric solenoid valve will open upon activation of the electrical supplemental detection system and a low air pressure alarm caused by an opening of a sprinkler head.  The opening of the deluge valve shall not be dependent on the order of activation of the release devices, only that both devices must activate before the deluge valve will open.  The preaction system riser shall be of a listed and approved assembly.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The Preaction System shall be of a Double Interlock Release type.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Water Control Valve

The deluge systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The deluge valve shall be externally resettable by hydraulic means.  The deluge valve shall employ a positive vent on the priming line to ensure that the deluge valve will not prematurely reset.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no cases less than 175 PSI.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

Detection

The detection shall be of the cross-zoned type.  The electric detection system and the low air pressure alarm will be required prior to the opening of the normally closed solenoid valve, thereby, releasing the deluge valve prime pressure.  Activation of one zone of detectors (electric detector or low air supervisory switch) will cause an alarm in the zone but release will not occur until the second zone is activated.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

- Electric fixed temperature self-restoring releases.  (Insert applicable product specification.)

- Electric smoke detection devices.  Smoke detection devices to be compatible with system control panel.  (Insert applicable product specification.)

Release Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Normally Closed Solenoid Valve

The deluge valve priming water release device shall be an electrically operated normally closed solenoid valve.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves and Viking Model H or J Flow Control Valves.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, part number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the system riser.

D.	A riser mounted compressor listed as an air maintenance compressor.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Quick Opening Device:

If water cannot be delivered to the dry system inspectors test connection within a minute of opening, a quick opening device shall be provided on the system riser.  The quick opening device shall be of the same manufacturer as the dry pipe valve.  The sprinkler system quick opening device shall be an accelerator with an external anti-flooding device.  Accelerator manufacturer to be The Viking Corporation.  Accelerator to be Viking Model E-1.

Model LD-1 Anti-Column Device:

The anti-column device shall have a stainless steel body and shall utilize a stainless steel float ball which rises when water in the system accumulates to the level of the anti-column device. When the float ball rises, water is automatically drained from the system. The anti-column device shall be UL listed and FM approved. The anti-column device shall be manufactured by the Viking Corporation. Anti-column Device Model to be Viking LD-1.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials or accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

TrimPac®  Surefire® Preaction System (Single Interlocked)

A failsafe preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by an activation of the electrical detection system only.  The preaction system shall be of a listed and approved assembly and the manufacturer’s components shall not be modified.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The failsafe preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the most current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The failsafe preaction system shall be of the Single Interlock Release type.

Note:  If the electrical release system design requires the use of a “cross-zone” configuration additional consideration must be given to the Viking VFR400 Multi-Hazard Release Control Panel and its capabilities.  To accomplish a “cross-zone” configuration the system design must designate this function to be provided from the Building Fire Alarm Control Panel (FACP).  The initiating devices for area protected by the Surefire preaction system shall be attached to the building (FACP) in a cross zoned configuration.  Upon activation of the “cross-zoned” detection the (FACP) will send the initiating signal to input number 1 on the Surefire Release Panel and activate the system.

- System operation

The integrated VFR-400 release control panel sequence of operation shall be factory-programmed to perform the following:

A.	The activation of the electric detection is necessary to cause the deluge valve actuation.

B.	The activation of the detection condition alone will activate the solenoid valve open, causing the deluge valve to open and allowing water to enter the system piping. The alarm pressure switch will activate. Water will not discharge into the protected area since all sprinkler heads are closed.

C.	The opening of an automatic sprinkler OR damage to system piping without the detection condition satisfied will activate the "very low air" alarm pressure switch but water will not enter the system piping.

D.	The activation of the electric detection alone will activate the solenoid valve open, causing the deluge valve to open and allowing water to enter the system piping AND the opening of an automatic sprinkler will cause the water to flow out of any open sprinklers and/or any openings on the system.

E.	Operation of the emergency manual release will depressurize the priming chamber, causing the deluge valve to open and allowing water to enter the system piping. The alarm pressure switch will activate, Water will flow out of any open sprinklers and/or any openings on the system.

F.	When AC Power and DC power supplied by the back up batteries is lost, the system shall “fail-safe” and function as a dry pipe system. The normally open solenoid will remain open, and the pneumatic actuator is the only device holding the priming water in the priming chamber. When a sprinkler operates, air pressure is lost and the pneumatic actuator opens. Priming water is drained from the priming chamber, causing the deluge valve to open and allowing water to enter the system piping. The alarm pressure switch will activate. Water will flow out of any open sprinklers and/or any openings on the system.

G.	Trouble condition on detection zones, or "very low air" alarm zone, or the normally closed solenoid output disables the normally open solenoid and the pneumatic actuator is the only device holding the priming water in the priming chamber. When a sprinkler operates, air pressure is lost and the pneumatic actuator opens. Priming water is drained from the priming chamber, causing the deluge valve to open and allowing water to enter the system piping. The alarm pressure switch will activate. Water will flow out of any open sprinklers and/or any openings on the system.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Viking Trimpac® Single Interlock Preaction

The deluge valve trim shall be a trim package for a deluge valve with a specific release device and release module for the desired application manufactured and tested in a metal enclosure.  The metal enclosure shall be 16-gauge steel painted with a red epoxy powder coat.  The standard trim normally required on a deluge valve will be enclosed in this single cabinet.  The Trimpac shall provide access doors for the emergency release and alarm test valve for manual operation of these trim valves.  The Trimpac shall be equipped with priming water pressure and water supply gauge view-ports for easy monitoring of water pressures.  The enclosure shall be designed to protect the trim valves from inadvertent operation.  The system shall be piped (or use the stainless steel hose package) from the valve body to the enclosure assembly.  The Trimpac Model D-1 can be utilized for single interlocked preaction systems with the Viking Model E-1 or F-1 Deluge Valves in all sizes.  The unit shall be rated for 250 PSI (1724 kPa).  The Deluge Valve Trim shall be Viking Trimpac Double Interlocked Preaction Pneumatic Model D-1, part number 13798D-1.

Water Control Valve

The deluge or preaction systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The Deluge valve shall be capable for installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Control Valve

The failsafe preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

Pneumatic Actuator

Preaction or deluge systems utilizing pneumatic release detectors shall employ a pneumatic actuator between the detection and the operating systems.  The device shall actuate a release in the deluge valve priming water supply.  The actuator of the pneumatic release system shall be UL Listed and Factory Mutual Approved for use with the deluge valve installed.  The Pneumatic Actuator manufacturer to be The Viking Corporation.  Pneumatic Actuator to be Viking Model H-1.

Normally Open Solenoid Valve

The deluge valve priming water release device shall be an electrically operated Normally Open solenoid valve when electric releases are used as the supplemental detection system.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves.

Normally Closed Solenoid Valve

The deluge valve priming water release device shall be an electrically operated Normally closed solenoid valve when electric releases are used as the supplemental detection system.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Supplemental Detection System

A supplemental detection system shall be provided for all preaction systems.  Acceptable supplemental detection devices are:

A.	Electric fixed temperature self-restoring releases.  (Insert applicable product specification.)

B.	Electric smoke detection devices.  Smoke detection devices to be compatible with system control panel.  (Insert applicable product specification.)

C.	Other compatible listed electrical detectors.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Model LD-1 Anti-Column Device:

The anti-column device shall have a stainless steel body and shall utilize a stainless steel float ball which rises when water in the system accumulates to the level of the anti-column device. When the float ball rises, water is automatically drained from the system. The anti-column device shall be UL listed and FM approved. The anti-column device shall be manufactured by the Viking Corporation. Anti-column Device Model to be Viking LD-1.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials

and accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.

VIKING SYSTEM SPECIFICATIONS

PREACTION SYSTEMS

TrimPac® Surefire® Preaction System (Double Interlocked)

A failsafe preaction system shall be provided.  The method of release of the deluge valve priming water pressure shall be by an activation of the electrical detection system only.  The failsafe preaction system shall be of a listed and approved assembly and the manufacturer’s components shall not be modified.  The system riser shall be equipped with a rubber seated check valve downstream of the deluge valve and prior to the supervisory air connection.  The preaction system shall be provided with all necessary appurtenances to complete the system.  The system shall be installed in conformance with the most current Edition of N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The failsafe preaction system shall be of the Double Interlock Release type.

Note:  If the electrical release system design requires the use of a “cross-zone” configuration additional consideration must be given to the Viking VFR400 Multi-Hazard Release Control Panel and its capabilities.  To accomplish a “cross-zone” configuration the system design must designate this function to be provided from the Building Fire Alarm Control panel (FACP).  The initiating devices for area protected by the Surefire preaction system shall be attached to the building (FACP) in a cross zoned configuration.  Upon activation of the “cross-zoned” detection the (FACP) will send the initiating signal to input number 1 on the Surefire Release Panel and activate the system.

- System operation

The integrated VFR-400 releasing control panel sequence of operation shall be factory-programmed to perform the following:

A.	The activation of the electric detection AND the opening of an automatic sprinkler is necessary to cause the deluge valve actuation.

B.	The activation of the electric detection alone will not cause water to enter the system piping.

C.	The opening of an automatic sprinkler OR damage to system piping without the detection condition satisfied will activate the "very low air" alarm pressure switch but water will not enter the system piping.

D.	Activation of the electric detection AND the "very low air" alarm pressure switch will activate the solenoid valve open, causing the deluge valve to open and allowing water to enter the system piping. The alarm pressure switch will activate. Water will flow out of any open sprinklers and/or any openings on the system.

E.	Operation of the emergency manual release will depressurize the priming chamber, causing the deluge valve to open and allowing water to enter the system piping. The alarm pressure switch will activate, Water will flow out of any open sprinklers and/or any openings on the system.

F.	When AC Power and DC power supplied by the back up batteries is lost, the system shall “fail-safe” and function as a dry pipe system. The normally open solenoid will remain open, and the pneumatic actuator is the only device holding the priming water in the priming chamber. When a sprinkler operates, air pressure is lost and the pneumatic actuator opens. Priming water is drained from the priming chamber, causing the deluge valve to open and allowing water to enter the system piping. The alarm pressure switch will activate. Water will flow out of any open sprinklers and/or any openings on the system.

G.	Trouble condition on detection zones, or "very low air" alarm zone, or the normally closed solenoid output will disable the normally open solenoid and the pneumatic actuator is the only device holding the priming water in the priming chamber. When a sprinkler operates, air pressure is lost and the pneumatic actuator opens. Priming water is drained from the priming chamber, causing the deluge valve to open and allowing water to enter the system piping. The alarm pressure switch will activate. Water will flow out of any open sprinklers and/or any openings on the system.

SYSTEM DEVICES

MANUFACTURERS

A. 	Sprinklers, Valves, and Equipment:

1. 	Viking Corporation: www.vikinggroupinc.com

2. 	Substitutions: Not permitted.

Viking Trimpac® Double Interlock Preaction

The deluge valve trim shall be a trim package for a deluge valve with a specific release device and release module for the desired application manufactured and tested in a metal enclosure.  The metal enclosure shall be 16-gauge steel painted with a red epoxy powder coat.  The standard trim normally required on a deluge valve will be enclosed in this single cabinet.  The Trimpac shall provide access doors for the emergency release and alarm test valve for manual operation of these trim valves.  The Trimpac shall be equipped with priming water pressure and water supply gauge view-ports for easy monitoring of water pressures.  The enclosure shall be designed to protect the trim valves from inadvertent operation.  The system shall be piped (or use the stainless steel hose package) from the valve body to the enclosure assembly.  The Trimpac Model D-2 can be utilized for double interlocked preaction systems with the Viking Model E-1 or F-1 Deluge Valves in all sizes.  The unit shall be rated for 250 PSI (1724 kPa).  The Deluge Valve Trim shall be Viking Trimpac Double Interlocked Preaction Pneumatic Model D-2, part number 13799D-2.

Water Control Valve

The deluge or preaction systems shall utilize a 90° pattern or straight-through pattern type of deluge valve.  The inlet and outlet connections of deluge valve can be flanged by flanged, flanged by grooved, grooved by grooved or thread by thread, respectively.  The deluge valve shall be capable of installation in the vertical or horizontal position.  The deluge valve shall be UL Listed and Factory Mutual Approved.  The deluge valve shall have a working pressure of 250 PSI.  The valve trim shall be compatible and shall be installed following the manufacturer’s specifications.  The Deluge Valve manufacturer to be The Viking Corporation.  Deluge Valve to be Viking Model E-1 or F-1.

System Control Valve

The preaction system control valve shall be a listed indicating type valve.  The control valve shall be UL Listed and Factory Mutual Approved for fire protection installations.  The system control valve shall be rated for normal system pressure but in no case less than 175 PSI.

System Check Valve

Check valves shall be UL Listed and Factory Mutual Approved for use on fire protection systems.  The sprinkler riser check valves shall be manufactured with supply side and system side gauge connections and a main drain outlet in conformance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The check valves shall be constructed of a ductile iron body with a brass seat and a rubber faced clapper assembly hinged to a removable access cover.  The check valves shall be equipped with a removable access cover for periodic inspection as required in N.F.P.A. 25, Standard for Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.  The check valves shall have a working water pressure of 250 PSI.  The Check Valve manufacturer to be The Viking Corporation.  The Check Valve to be Viking Model F-1 Easy Riser Check Valve or Model L-1 or K-1 In-Line Check Valve.

Pneumatic Actuator

Preaction or deluge systems utilizing pneumatic release detectors shall employ a pneumatic actuator between the detection and the operating systems.  The device shall actuate a release in the deluge valve priming water supply.  The actuator of the pneumatic release system shall be UL Listed and Factory Mutual Approved for use with the deluge valve installed.  The Pneumatic Actuator manufacturer to be The Viking Corporation.  Pneumatic Actuator to be Viking Model H-1.

Release Control Panel

The system release panel shall be capable of a dual hazard split release, dual hazard combined release, single hazard cross-zone release, single hazard two-zone release.  The release panel shall be equipped with a local tone alarm to annunciate loss of A/C power, system trouble, circuit trouble and low auxiliary D/C power supply.  The release panel shall be capable of supervising trouble and alarm audible alarms.  The trouble and alarm audible alarms shall be able to be silenced at release panel.  The release panel shall be housed in a vented enclosure with ambient temperature compatibility of 32°F to 120°F.  The panel enclosure shall be of adequate size to house auxiliary D/C power supply.  The auxiliary D/C power supply shall consist of (2) 12-volt lead acid batteries of the same ampere-hour rating.  Actual ampere-hour rating to be established by auxiliary D/C power requirement.  The Release Panel shall be a Viking VFR400 Multi-Hazard Release Control Panel.

Supplemental Detection System

A supplemental detection system shall be provided for all failsafe preaction systems.  Acceptable supplemental detection devices are:

A.	Electric fixed temperature self-restoring releases.  (Insert applicable product specification.)

B.	Electric smoke detection devices.  Smoke detection devices to be compatible with system control panel.  (Insert applicable product specification.)

C.	Other compatible listed electrical detectors.

Pressure Supervisory Switch

A supervisory air pressure shall be maintained on all preaction systems with 20 sprinklers or more on the system piping.  A low air pressure alarm will activate by way of a pressure supervisory alarm pressure switch.  The low air pressure alarm switch shall be compatible with system devices.  The low air pressure alarm switch enclosure shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The low air pressure alarm switch shall have the ability to be wired for Class A or Class B service.  The Low Air Pressure Supervisory Switch shall be Potter, model number PS401A or PS402A.

Alarm Pressure Switch

Water flow will activate an alarm by way of an alarm pressure switch.  The alarm pressure switch shall be compatible with the system devices.  The alarm pressure enclosure shall be UL Listed and Factory Mutual Approved.  The alarm pressure switch shall have the ability to be wired for Class A or Class B service.  The Alarm Pressure Switch shall be Potter, model number PS101A or PS102A.

Normally Open Solenoid Valve

The deluge valve priming water release device shall be an electrically operated Normally Open solenoid valve when electric releases are used as the supplemental detection system.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves.

Normally Closed Solenoid Valve

The deluge valve priming water release device shall be an electrically operated Normally closed solenoid valve when electric releases are used as the supplemental detection system.  The solenoid valve shall be constructed of a ½" brass body with a stainless steel core tube, core, plugnut and springs.  The solenoid valve shall have a maximum working pressure of 250 PSI.  The solenoid valve shall be UL Listed for its intended use.  The Solenoid Valve shall be listed for use with Viking Model E or F Deluge Valves.

Sprinklers

- Store sprinkler system components in their original shipping container, in a clean, dry space protected from weather. Until completion of all finish-out, protective caps/clips shall not be removed from sprinklers or cover plates/escutcheon plates installed. Any painted sprinklers or cover plates shall be replaced.

- Fire sprinklers shall be of one manufacturer throughout the building.  No mixing of sprinkler brands shall be permitted.  Sprinklers shall be of all brass frame construction utilizing a metal Belleville spring seal, coated on both sides with Teflon film.  Utilization of non-metal parts in the sealing portion of the sprinkler is strictly prohibited.

- To reduce water delivery times by way of faster system air discharge, sprinklers incorporating stepped orifice designs shall be selected where possible.

- The following sprinkler types and arrangements shall be allowed:

  - Upright sprinklers

  - Listed dry sprinklers

  - Pendent sprinklers and sidewall sprinklers installed on return bends, where the sprinkler, return bend, and branch line piping is in an area maintained at or above 40°F (4°C)

  - Horizontal sidewall sprinklers, installed so that water is not trapped.

Compressed Air Supply

An air supply capable of restoring system pressure within 30 minutes shall be provided.  Acceptable air supply arrangements are:

A.	Owner supplied air system with an air maintenance device on the supply side of the air supply inlet.

B.	A tank mounted air compressor with an air maintenance device between the air compressor and the air supply inlet on the system riser.

C.	A riser mounted air compressor feeding an air reservoir.  An air maintenance device shall be placed between the air reservoir and the air supply inlet on the system riser.

Dehydrator:

When air supplies for dry pipe or preaction sprinkler systems are subject to moisture or condensation into the system piping, an air dehydrator shall be installed in the air supply piping to the system.  The air dehydrator shall be equipped with a means of visually indicating if the medium used to remove moisture is saturated.  Air dehydrator shall have a drying capacity of 4400 sc ft of air at -45°F and be capable of maximum air flow of 10 sc ft/min at 100 PSI.  Air Dehydrator manufacturer shall be The Viking Corporation, part number 16854.

Air Maintenance Device

Air supplies provided for sprinkler systems shall be equipped with an automatic air pressure maintenance device.  The air maintenance device shall be equipped with a ¼" air supply bypass with a field adjustable air pressure regulator with a built in ball check valve to eliminate air loss when system is in service.  The air maintenance device shall have a factory setting of 40 PSI.  The Air Maintenance Device manufacturer to be The Viking Corporation.  Air Maintenance Device to be Viking Model D-2.

Quick Opening Device:

If water cannot be delivered to the dry system inspectors test connection within a minute of opening, a quick opening device shall be provided on the system riser.  The quick opening device shall be of the same manufacturer as the dry pipe valve.  The sprinkler system quick opening device shall be an accelerator with an external anti-flooding device.  Accelerator manufacturer to be The Viking Corporation.  Accelerator to be Viking Model E-1.

Model LD-1 Anti-Column Device:

The anti-column device shall have a stainless steel body and shall utilize a stainless steel float ball which rises when water in the system accumulates to the level of the anti-column device. When the float ball rises, water is automatically drained from the system. The anti-column device shall be UL listed and FM approved. The anti-column device shall be manufactured by the Viking Corporation. Anti-column Device Model to be Viking LD-1.

Water Motor Alarm

Water flow will activate a hydraulic powered water motor alarm by way of integral valve alarm line trim piping.  The water motor alarm shall be connected to a water pressure retarding chamber to limit the propensity of unnecessary alarms.  The water motor alarm shall be equipped with a rear closure plate to limit the access of foreign materials or

accumulation of debris.  The water motor alarm shall be UL Listed and Factory Mutual Approved for the application in which it is used.  The Water Motor Alarm manufacturer to be The Viking Corporation.  Water Motor Alarm to be Viking Model F-2 or G-2.  (G-2 not UL Listed or FM Approved)

Fire Department Connection

A system fire department connection shall be provided on the system riser in accordance with N.F.P.A. 13, Standard for Installation of Sprinkler Systems.  The fire department connection shall be of a brass body with an integral clapper assembly to separate flow between inlets.  The fire department connection shall be installed in an area accessible for the first response unit.  The fire department connection shall be UL Listed and Factory Mutual Approved for fire protection use.