## Vik Data 2
|  | The Viking Corporation 210 N. Industrial Park Drive Hastings, Michigan 49058 U.S.A. |  |  | Technical Services Toll-Free: 877-384-5464 Fax: 269-818-1680 Web Site: http://www.vikinggroupinc.com | Domestic Sprinkler Selection Guide | [5 empty] | Revised 4/14
THIS CHART HAS BEEN DEVELOPED TO ASSIST IN THE SELECTION OF THE APPROPRIATE VIKING SPRINKLERS. TO SELECT A SPRINKLER, YOU MUST CHOOSE THE HAZARD APPLICATION OF THE PROJECT. THEN REFER TO THAT SECTION FOR THE DESIRED SPRINKLER SELECTION.
THIS CHART IS NOT INTENDED TO BE A STAND-ALONE GUIDE FOR SELECTING A SPECIFIC SPRINKLER. ALWAYS REFER TO THE CURRENT SPECIFIC VIKING TECHNICAL DATA PAGE FOR DETAILED INFORMATION ON ANY VIKING SPRINKLER HEAD.
Occupancy | Sprinkler Model and Type | SIN | Response* | Max. | Available Temperature Ratings | Minimum | Maximum | Orifice | Nominal | Thread | Available Finishes ** | Listings and Approvals * | Data
Type |  |  | Std, Quick, Res | PSI | in Degrees Fahrenheit (F) | Spacing | Spacing | Size | K Factor | Size |  |  | Page No.
Residential | NOTE: All of the following listings are for residential sprinklers manufactured on or after July 12, 2002.
| M-4 Residential Pendent (Rec) | VK430 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 4.3 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC, NSF | 141o-t
| Residential Upright | VK467 | Residential | 175 | 155° 175° | 12' x 12' | 16' x 16' | Small | 4.9 | 1/2" | Br, Chr, Wht, Blk, ENT | cULus, NYC, NSF | 158a-e
| Residential Pendent (Rec) | VK466 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 5.2 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC††, NSF | 141j-p
| Residential Pendent (Rec) | VK458 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Large | 7.4 | 3/4" | Br, Chr, Wht, Blk | cULus, NYC, NSF | 140u-z
| Residential Pendent (Rec) | VK468 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC, NSF | 149m-t
| Residential Lead Free Pendent (Rec) | VK4680 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC††, NSF | 152h-o
| Residential Pendent (Rec) | VK470 | Residential | 175 | 155° 175° | 12' x 12' | 16' x 16' | Small | 3 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 153g-j
| Residential Pendent (Rec) | VK4700 | Residential | 175 | 155° 175° | 12' x 12' | 16' x 16' | Small | 3 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 154u-x
| Residential Pendent (Rec) | VK472 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Standard | 5.8 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 148o-r
| Residential HSW (Rec) | VK484 | Residential | 175 | 155° 175° | 12' x 12' | 16' x 20' | Standard | 4.2 | 1/2" | Br, Chr, Wht, Blk | ` | 144h-m
| Residential Lead Free HSW (Rec) | VK4840 | Residential | 175 | 155° 175° | 12' x 12' | 16' x 20' | Standard | 4.2 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC††, NSF | 144o-t
| Residential HSW (Rec) | VK460 | Residential | 175 | 155° 175° | 12' x 12' | 14' x 26' | Standard | 5.8 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC, NSF | 152a-h
| Residential HSW (Rec) | VK486 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Standard | 4 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 156u-z
| H-3 Residential Flush Pendent | VK420 | Residential | 175 | 165° (220° No Approvals) | 12' x 12' | 16' x 16' | Small | 3.8 | 1/2" | Chr, Wht | FM, NYC†† | 145a-b
| Residential Concealed Pendent | VK466 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 5.2 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC, NSF | 141r-w
| Residential Concealed Pendent | VK458 | Residential | 175 | 155° | 12' x 12' | 20' x 20' | Large | 7.4 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC, NSF | 142u-z
| Residential Concealed Pendent | VK474 | Residential | 175 | 165° | 12' x 12' | 20' x 20' | Standard | 5.8 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC†† | 148h-l
| Residential Concealed Lead Free Pendent | VK4740 | Residential | 175 | 165° | 12' x 12' | 20' x 20' | Standard | 5.8 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC††, NSF | 149a-e
| Residential Concealed Pendent | VK468 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC, NSF | 150u-z
| Residential Flush Pendent | VK476 | Residential | 175 | 165° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Wood Beam Finish, Wht, Blk | cULus, NYC†† | 145h-m
| Residential Concealed Pendent | VK457 | Residential | 175 | 165° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC, NSF | 147u-z
| Residential Concealed Lead Free Pendent | VK4570 | Residential | 175 | 165° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC††, NSF | 151h-m
| Residential Concealed HSW | VK480 | Residential | 175 | 165° | 12' x 12' | 16' x 18' | Small | 4 | 1/2" | Wht | cULus, NYC†† | 153a-f
| Residential Concealed Lead Free HSW | VK4800 | Residential | 175 | 165° | 12' x 12' | 16' x 18' | Small | 4 | 1/2" | Wht | cULus, NYC†† | 151q-v
| Residential Concealed Pednent | VK488 | Residential | 175 | 165° | 12' x 12' | 16' x 16' | Small | 3 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC††, NSF | 157a-e
NOTE: The following listings are for residential sprinklers to be used as replacement sprinklers in existing systems, or for system designs using residential sprinklers manufactured prior to July 12, 2002.
| M-4 Residential Pendent (Rec) | VK430 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 4.3 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC | 141o-t
| H-3 Residential Flush Pendent | VK420 | Residential | 175 | 165° (220° No Approvals) | 12' x 12' | 20' x 20' | Small | 3.8 | 1/2" | Chr, Wht | cULus, FM, NYC | 145a-b
Beamed | Residential Pendent (Rec) | VK466 | Residential | 175 | 155° | 12' x 12' | 20' x 20' | Small | 5.2 | 1/2" | Br, Chr, Wht, Blk | cULus, NSF | 141j-p
Residential | Residential Pendent (Rec) | VK468 | Residential | 175 | 155° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC, NSF | 149m-t
| Residential Lead Free Pendent (Rec) | VK4680 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC††, NSF | 152h-o
| Residential Flush Pendent | VK476 | Residential | 175 | 165° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Wood Beam Finish, Wht, Blk | cULus | 145h-m
Sloped | NOTE: All of the following listings are for residential sprinklers manufactured on or after July 12, 2002.
Residential | M-4 Residential Pendent (Rec) | VK430 | Residential | 175 | 155° 175° | 12' x 12' | 16' x 16' | Small | 4.3 | 1/2" | Br, Chr, Wht, Blk | UL, NYC, NSF | 141o-t
| Residential Pendent (Rec) | VK466 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 5.2 | 1/2" | Br, Chr, Wht, Blk | UL, NYC, NSF | 141j-p
| Residential Pendent (Rec) | VK458 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Large | 7.4 | 3/4" | Br, Chr, Wht, Blk | UL, NYC, NSF | 140u-z
| Residential Pendent (Rec) | VK468 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Br, Chr, Wht, Blk | UL, NYC, NSF | 149m-t
| Residential Lead Free Pendent (Rec) | VK4680 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC††, NSF | 152h-o
| Residential HSW (Rec) | VK484 | Residential | 175 | 155° | 16' x 16' | 16' x 18' | Standard | 4.2 | 1/2" | Br, Chr, Wht, Blk | UL, NYC††, NSF | 144h-m
| Residential Lead Free HSW (Rec) | VK4840 | Residential | 175 | 155° | 16' x 16' | 16' x 18' | Standard | 4.2 | 1/2" | Br, Chr, Wht, Blk | UL, NYC††, NSF | 144o-t
| Residential Concealed Pendent | VK466 | Residential | 175 | 155° 175° | 12' x 12' | 20' x 20' | Small | 5.2 | 1/2" | Chr, Wht, Iv, Blk | UL, NYC††, NSF | 141r-v
| Residential Concealed Pendent | VK458 | Residential | 175 | 155° | 12' x 12' | 20' x 20' | Large | 7.4 | 3/4" | Chr, Wht, Iv, Blk | UL, NYC, NSF | 142u-z
| Residential Concealed Pendent | VK468 | Residential | 175 | 155° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Chr, Wht, Iv, Blk | UL, NYC††, NSF | 150u-z
| Residential Flush Pendent | VK476 | Residential | 175 | 165° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Wood Beam Finish, Wht, Blk | UL, NYC†† | 145h-m
| Residential Concealed Pendent | VK457 | Residential | 175 | 165° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Chr, Wht, Iv, Blk | UL, NYC, NSF | 147u-z
| Residential Concealed Lead Free Pendent | VK4570 | Residential | 175 | 165° | 12' x 12' | 20' x 20' | Small | 4.9 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC††, NSF | 151h-m
NOTE: The following listings are for residential sprinklers to be used as replacement sprinklers in existing systems, or for system designs using residential sprinklers manufactured prior to July 12, 2002.
| M-4 Residential Pendent (Rec) | VK430 | Residential | 175 | 155° 175° | 12' x 12' | 16' x 16' | Small | 4.3 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC | 141o-t
| H-3 Residential Flush Pendent | VK420 | Residential | 175 | 165° (220° No Approvals) | 12' x 12' | 18' x 18' | Small | 3.8 | 1/2" | Chr, Wht | cULus, NYC | 145a-b
Light Hazard† | M SSU | VK001 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA, FM | Per NFPA, FM | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC†† | 11a-h | 12a-f
Only | M SSU | VK002 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, NYC†† | 11a-h
| M HP SSU | VK021 | Standard | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 11a-h
| M SSP (Rec)* | VK003 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA, FM | Per NFPA, FM | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC†† | 11a-h | 12a-f
| M SSP (Rec)* | VK004 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, NYC†† | 11a-h
| M HP SSP (Rec)* | VK023 | Standard | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 11a-h
| M HSW (Rec)* | VK104 | Standard | 175 | 135°155° 175° 200° 286° 360° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC | 14e-j | 14u-z
| M HP HSW (Rec)* | VK015 | Standard | 250 | 135°155° 175° 200° 286° 360° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 14e-j
| M VSW | VK106 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr | FM, NYC†† | 14a-b | 14u-z
| M Fusible Link SSU | VK006 | Standard | 175 | 165° 220° 286° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, NYC | 18a-f
| M Fusible Link SSP (Rec)* | VK008 | Standard | 175 | 165° 220° 286° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br, Chr, Wx | cULus, NYC | 18a-f
| M Fusible Link HSW (Rec)* | VK112 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wx | cULus, FM, NYC†† | 19a-e | 19u-z
| M QR SSU | VK325 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 51a-e | 41u-z
| QR Fusible Element SSU | VK326 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 42h-m | 51h-k
| M QR SSU | VK327 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 51a-e
| QR Fusible Element SSU | VK328 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 51h-k
| QR COINTM Upright (Specific Application) | VK900 | Quick | 175 | 175° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br | cULus, NYC†† | 112a-i
| QR COINTM Fusible Element Upright (Specific Application) | VK901 | Quick | 175 | 205° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br | cULus, NYC†† | 112r-z
| M QR HP SSU | VK340 | Quick | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 51a-e
| QR HP Fusible Element SSU | VK341 | Quick | 250 | 165° 205° 280° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 51h-k
| M QR SSP (Rec)* | VK329 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 41a-e | 41u-z
| M QR SSP (Rec)* | VK331 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 41a-e
| QR Fusible Element SSP (Rec)* | VK332 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 40a-f
| M QR HP SSP (Rec)* | VK342 | Quick | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 41a-e
| QR HP Fusible Element SSP (Rec)* | VK343 | Quick | 250 | 165° 205° 280° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 40a-f
| M-5 QR HSW | VK305 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | cULus, FM, NYC†† | 43a-f | 43u-z
| QR Fusible Element HSW | VK308 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | cULus, FM, NYC†† | 43h-m | 52o-t
Light Hazard† | QR Fusible Element HSW (Rec)* | VK307 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 52o-t | 52u-z
Only (continued) | M QR HSW (Rec)* | VK333 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 52a-f
| QR Fusible Element HSW (Rec)* | VK334 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 52u-z
| M QR HP HSW (Rec)* | VK344 | Quick | 250 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 52a-f
| QR HP Fusible Element HSW (Rec)* | VK346 | Quick | 250 | 165° 205° 280° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 52u-z
| M QR VSW | VK306 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr | FM, NYC†† | 52e-h
| QR Fusible Element VSW | VK309 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr | FM, NYC†† | 50a-d
| QR Concealed Pendent | VK461 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Small | 2.8 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | cULus, NYC | 54h-l
| QR Adjustable Concealed Pendent | VK461 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Small | 2.8 | 1" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | cULus, NYC†† | 140a-c
| QR Concealed Pendent | VK465 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Small | 4.2 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC†† | 64a-e
| QR Adjustable Concealed Pendent | VK465 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Small | 4.2 | 1" | Chr, Wht, Iv, Blk | cULus, NYC†† | 140a-c
| QREC Concealed Pendent | VK632 | Quick | 175 | 135°155° 175° 200° | 16' x 16' | 20' x 20' | Standard | 5.6 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC†† | 92a-f
| QREC Concealed Pendent | VK634 | Quick | 175 | 135°155° 175° 200° | 16' x 16' | 20' x 20' | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 92a-f
| Concealed Pendent | VK461 | Standard | 175 | 155° 175° 200° | Per NFPA, FM | Per NFPA, FM | Small | 2.8 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | FM, NYC†† | 54h-l
| M EC SSP (Rec)* | VK600 | Standard | 175 | 155° 175° | 16' x 16' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC | 81a-f
| M EC SSP (Rec)* | VK602 | Standard | 175 | 155° 175° | 16' x 16' | 20' x 20' | Large | 8 | 3/4" | Br, Chr, Wht, Blk | cULus, NYC | 81a-f
| M-5 EC SSP (Rec)* | VK604 | Standard | 175 | 155° 175° | 18' x 18' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 90e-j
| EC Fusible Element SSP (Rec)* | VK607 | Standard | 175 | 165° 205° | 18' x 18' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 90v-z
| M-5 HP EC SSP (Rec)* | VK610 | Standard | 250 | 155° 175° | 18' x 18' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 90e-j
| HP EC Fusible Element SSP (Rec)* | VK611 | Standard | 250 | 165° 205° | 18' x 18' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 90v-z
| EC Fusible Element HSW (Rec)* | VK615 | Standard | 175 | 165° 205° | 16' x 16' | 16' x 24' | Large | 8 | 3/4" | Br, Chr, Wht, Blk | FM, NYC†† | 82v-z
| M-5 EC HSW (Rec) | VK605 | Standard | 175 | 155° | 16' x 16' | 16' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 91a-f
| EC Fusible Element HSW (Rec) | VK609 | Standard | 175 | 165° 205° | 16' x 16' | 16' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 91h-m
| M-5 HP EC HSW (Rec) | VK612 | Standard | 250 | 155° | 16' x 16' | 16' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 91a-f
| HP EC Fusible Element HSW (Rec) | VK613 | Standard | 250 | 165° | 16' x 16' | 16' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 91h-m
| EC Concealed SSP | VK614 | Standard | 175 | 155° | 18' x 18' | 20' x 20' | Standard | 5.6 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC†† | 88a-f
| EC Concealed SSP | VK616 | Standard | 175 | 155° | 18' x 18' | 20' x 20' | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 88a-f
| EC Concealed ELO SSP | VK618 | Standard | 175 | 155° | 18' x 18' | 20' x 20' | Extra Large | 11.2 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 86a-f
| M EC ELO SSP (Rec)* | VK608 | Standard | 175 | 155° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC | 85a-f
| EC ELO Fusible Element SSP (Rec)* | VK617 | Standard | 175 | 165° 205° | 12' x 12' | 14' x 14' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 85h-m
| M QR EC SSP (Rec)* | VK600 | Quick | 175 | 135° 155° 175° | 16' x 16' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, FM, NYC | 81a-f
| QR EC Fusible Element SSP (Rec)* | VK601 | Quick | 175 | 165° 205° (FM 165°) | 16' x 16' | 18' x 18' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, FM, NYC†† | 81h-l
| M QR EC SSP (Rec)* | VK602 | Quick | 175 | 135° 155° 175° | 16' x 16' | 20' x 20' | Large | 8 | 3/4" | Br, Chr, Wht, Blk | cULus, FM, NYC | 81a-f
| QR EC Fusible Element SSP (Rec)* | VK603 | Quick | 175 | 165° 205° (FM 165°) | 16' x 16' | 18' x 18' | Large | 8 | 3/4" | Br, Chr, Wht, Blk | cULus, FM, NYC†† | 81h-l
| M-5 QR EC SSP (Rec)* | VK604 | Quick | 175 | 135° 155° 175° (20'x20' @ 135° 175°) | 16' x 16' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC | 90e-j
| QR EC Fusible Element SSP (Rec)* | VK607 | Quick | 175 | 165° 205° | 16' x 16' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 90v-z
| M-5 QR HP EC SSP (Rec)* | VK610 | Quick | 250 | 135° 155° 175° (20'x20' @ 135° 175°) | 16' x 16' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC | 90e-j
| QR HP EC Fusible Element SSP (Rec)* | VK611 | Quick | 250 | 165° 205° | 16' x 16' | 20' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 90v-z
| M QR EC HSW (Rec)* | VK606 | Quick | 175 | 135° 155° 175° | 16' x 16' | 16' x 24' | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 82a-f
| QR EC HSW (Rec)* | VK630 | Quick | 175 | 135° 155° 175° | 16' x 16' | 18' x 22' | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 80a-e
| M-5 QR EC HSW (Rec) | VK605 | Quick | 175 | 135° 155° 175° (slopes to 4/12) | 16' x 16' | 16' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 91a-f
| QR EC Fusible Element HSW (Rec) | VK609 | Quick | 175 | 165° 205° (slopes to 4/12) | 16' x 16' | 16' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 91h-m
| M-5 QR HP EC HSW (Rec) | VK612 | Quick | 250 | 135° 155° 175° | 16' x 16' | 16' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 91a-f
| QR HP EC Fusible Element HSW (Rec) | VK613 | Quick | 250 | 165° 205° | 16' x 16' | 16' x 20' | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 91h-m
| B-1 QR EC Concealed Pendent | VK625 | Quick | 175 | 165° (220° No Approvals) | 16' x 16' | 18' x 18' | Standard | 5.6 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | cULus, NYC | 87a-f
| B-2 QR EC Concealed Pendent | VK627 | Quick | 175 | 165° (220° No Approvals) | 16' x 16' | 18' x 18' | Large | 8 | 3/4" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | cULus, NYC | 87a-f
| B-2 QR EC Concealed Pendent (for retrofit only) | VK627 | Quick | 175 | 165° (220° No Approvals) | 16' x 16' | 18' x 18' | Large | 8 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | cULus, NYC | 87a-f
| QR EC Concealed SSP | VK614 | Quick | 175 | 135° 155° 175° | 16' x 16' | 20' x 20' | Standard | 5.6 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC†† | 88a-f
| QR EC Concealed SSP | VK616 | Quick | 175 | 135° 155° 175° | 16' x 16' | 20' x 20' | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 88a-f
| QR EC Concealed HSW | VK630 | Quick | 175 | 135° 175° | 16' x 16' | 18' x 22' | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC | 87h-m
| QR EC Concealed ELO SSP | VK618 | Quick | 175 | 135° 155° 175° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 86a-f
| QR EC Concealed ELO Fusible Element SSP | VK636 | Quick | 175 | 165° 205° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 89a-e
| M QR EC ELO SSP (Rec)* | VK608 | Quick | 175 | 135° 155° 175° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 85a-f
| QR EC ELO SSP (Rec)* | VK534 | Quick | 175 | 135° 155° 175° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 83a-f
| QR EC ELO SSU | VK532 | Quick | 175 | 135° 155° 175° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 83a-f
| QR EC ELO Fusible Element SSP (Rec)* | VK617 | Quick | 175 | 165° 205° (165° FM) | 16' x 16' | 18' x 18' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 85h-m
| QR EC HSW (Rec)* | VK638 | Quick | 175 | 135° 155° 175° 200° | 12' x 12' | 28' x 28' | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus | 84n-r
| QR EC HSW Concealed | VK638 | Quick | 175 | 135° 155° 175° 200° | 12' x 12' | 28' x 28' | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus | 84u-z
| QR EC Concealed HSW | VK680 | Quick | 175 | 165° | 14' x 22' | 18' x 22' | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC | 87n-q
| M Dry HSW (Std. Adj.) | VK156 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1" | Br, Chr, Wht | cULus, FM, NYC | 102a-h
| M Dry HSW (Rec. Adj.) | VK162 | Standard | 175 | 155° 175° 200° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1" | Br, Chr, Wht | cULus, FM, NYC | 102a-h
| M Dry HSW (Plain Brl.) | VK152 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1" | Br, Chr, Wht | cULus, FM, NYC | 102a-h
| M Dry VSW (Std. Adj.) | VK157 | Standard | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr | Not Listed | 103a-f
| M Dry VSW (Rec. Adj.) | VK161 | Standard | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr, Wht | Not Listed | 103a-f
| M Dry VSW (Plain Brl.) | VK153 | Standard | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Br, Chr | Not Listed | 103a-f
| M QR Dry HSW (Std. Adj.) | VK178 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr, Wht | cULus, NYC | 106a-g
| M QR Dry HSW (Rec. Adj.) | VK182 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr, Wht | cULus, NYC | 106a-g
| M QR Dry HSW (Plain Brl.) | VK174 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Br, Chr, Wht | cULus, NYC | 106a-g
| M EC Dry SSP (Rec) | VK186 | Standard | 175 | 155° 175° | 20' x 20' | 20' x 20' | Standard | 5.6 | 1" | Chr, Wht | cULus, NYC | 108a-f
| M QR EC Dry SSP (Rec) | VK186 | Quick | 175 | 155° 175° | 16' x 16' | 18' x 18' | Standard | 5.6 | 1" | Chr, Wht | cULus, NYC | 108a-f
| M EC Dry HSW (Rec) | VK188 | Standard | 175 | 155° 175° | 16' x 20' | 16' x 20' | Standard | 5.6 | 1" | Chr, Wht | cULus, NYC | 109a-f
| M QR EC Dry HSW (Rec) | VK188 | Quick | 175 | 155° 175° | 16' x 16' | 16' x 18' | Standard | 5.6 | 1" | Chr, Wht | cULus, NYC | 109a-f
| EC Dry Concealed SSP | VK196 | Standard | 175 | 155° | 18' x 18' | 20' x 20' | Standard | 5.6 | 1" | Chr, Wht, Iv, Blk | cULus, NYC | 108j-o
| QR EC Dry Concealed SSP | VK196 | Quick | 175 | 135° 155° 175° | 16' x 16' | 20' x 20' | Standard | 5.6 | 1" | Chr, Wht, Iv, Blk | cULus, NYC | 108j-o
| HQR-2 EC Institutional Pendent | VK410 | Quick | 175 | 165° 220° | Per NFPA | 16' x 16' | Standard | 5.6 | 1/2" | Chr | cULus, NYC†† | 126a-h
| HQR-2 Institutional HSW | VK412 | Quick | 175 | 165° (220° No Approvals) | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Chr | cULus, NYC | 126k-o
Light† and | M HP SSU | VK124 | Standard | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 11q-v
Ordinary Hazard | M HP SSP (Rec) | VK122 | Standard | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 11a-h
| M HP HSW (Rec)* | VK116 | Standard | 250 | 135°155° 175° 200° 286° 360° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 14e-j
| H Flush SSP | VK400 | Standard | 175 | 165° 220° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Chr, Wht | cULus, FM, NYC | 16a-d
| Concealed SSP | VK462 | Standard | 175 | 155° 175° 200° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | FM | 54a-e
| B-2 Concealed SSP | VK404 | Standard | 175 | 165° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | FM, NYC | 20a-e
| M QR SSU | VK300 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 51a-e | 41u-z
| M QR SSU | VK345 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | FM, NYC†† | 51a-e | 41u-z
| M QR SSU | VK350 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 51a-e
| M QR SSU (for retrofit only) | VK350 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 51a-e
| QR Fusible Element SSU | VK351 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 51h-k
| QR Fusible Element SSU (for retrofit only) | VK351 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 51h-k
| M HP QR SSU | VK300 | Quick | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 51a-e
| M HP QR SSU | VK315 | Quick | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 51a-e
Light† and | HP QR Fusible Element SSU | VK316 | Quick | 250 | 165° 205° 280° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 51h-k
Ordinary Hazard | M QR SSP (Rec)* | VK302 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 41a-e | 41u-z
(continued) | M QR SSP (Rec)* | VK352 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 41a-e
| QR Fusible Element SSP (Rec)* | VK353 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 40a-f
| QR Fusible Element SSP (Rec)* (for retrofit only) | VK353 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Large | 8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 40a-f
| M QR SSP (Rec)* (for retrofit only) | VK352 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 41a-e
| M HP QR SSP (Rec)* | VK317 | Quick | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 41a-e
| HP QR Fusible Element SSP (Rec)* | VK318 | Quick | 250 | 165° 205° 280° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 40a-f
| QR Fusible Element SSP (Rec)* | VK330 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Small | 2.8 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 42h-m
| QR SSU Stainless Steel | VK338 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Stainless Steel | cULus, NYC†† | 46a-d
| QR SSP Stainless Steel | VK339 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Stainless Steel | cULus, NYC†† | 46a-d
| QR ELO Fusible Element SSU | VK533 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 70w-z
| M QR ELO SSU | VK531 | Quick | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 70h-k
| M QR ELO SSP (Rec)* | VK377 | Quick | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 70a-e
| QR HSW (Rec)* | VK360 | Quick | 175 | 135° 155° 175° 200° | Per NFPA | Per NFPA | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 43o-t
| M-5 QR HSW (Rec)* | VK305 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 43a-f | 43u-z
| QR Fusible Element HSW (Rec)* | VK308 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC†† | 43h-m | 52o-t
| M-5 HP QR HSW (Rec)* | VK319 | Quick | 250 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC | 43a-f
| HP QR Fusible Element HSW (Rec)* | VK320 | Quick | 250 | 165° 205° 280° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 43h-m
| H QR Flush SSP | VK402 | Quick | 175 | 165° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Chr, Wht | cULus, FM, NYC | 53a-d
| M QR Conventional | VK310 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC | 51a-e
| QR Fusible Element Conventional | VK311 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, NYC†† | 51h-k
| M QR Conventional | VK354 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC | 51a-e
| QR Fusible Element Conventional | VK355 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Large | 8 | 3/4" | Br, Chr, Wht, Blk | cULus, NYC†† | 51h-k
| QR Fusible Element SSU | VK301 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, FM, NYC†† | 47a-f
| QR Fusible Element SSP (Rec)* | VK303 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk | cULus, FM, NYC†† | 47a-f
| QR Concealed SSP | VK302 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC†† | 41g-l
| B-2 QR Concealed SSP | VK404 | Quick | 175 | 165° 220° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | cULus, NYC | 20a-e
| Concealed SSP | VK302 | Standard | 175 | 155° 175° 200° | Per FM | Per FM | Standard | 5.6 | 1/2" | Chr, Wht, Iv, Blk | FM, NYC†† | 41g-l
| QR Concealed SSP | VK462 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | cULus, NYC | 54a-e
| QR Concealed MRI SSP | VK462 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC†† | 54p-t
| QR Concealed Cleanroom Large Cover | VK462 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC†† | 136g-k
| QR Adjustable Concealed SSP | VK462 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr, Wht, Iv, Blk | cULus, NYC†† | 140a-c
| HP QR Concealed SSP | VK463 | Quick | 250 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Chr, Wht, Iv, Blk | cULus, NYC | 54a-e
| LO QR Concealed SSP | VK464 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC | 55a-e
| LO QR Concealed MRI SSP | VK464 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 54p-t
| LO QR Concealed SSP | VK352 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 41g-l
| LO Concealed SSP | VK352 | Standard | 175 | 155° 175° 200° | Per FM | Per FM | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | FM, NYC†† | 41g-l
| LO QR Concealed Fusible Element SSP | VK353 | Quick | 175 | 165° 205° | Per NFPA | Per NFPA | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 42o-s
| LO Concealed Fusible Element SSP | VK353 | Standard | 175 | 165° 205° | Per FM | Per FM | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | FM | 42o-s
| QR Concealed HSW | VK481 | Quick | 175 | 165° 220° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | cULus, NYC | 63h-l
| QR Dry Flush Concealed Pendent SSP | VK482 | Quick | 175 | 165° 220° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr, Wht | cULus | 111a-g
| LO Dry HSW (Rec. Adj.) | VK254 | Standard | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 102s-z
| LO Dry HSW (Std. Adj.) | VK252 | Standard | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 102s-z
| LO Dry HSW (Plain Brl.) | VK250 | Standard | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Large | 8 | 1" | Br, Chr, Wht | cULus, NYC | 102s-z
| M QR Dry Upright | VK184 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Br, Wht | cULus, NYC | 107a-d
| M QR Dry SSP (Rec. Adj.) | VK180 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr, Wht | cULus, NYC | 105a-f
| M QR Dry SSP (Std. Adj.) | VK176 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr, Wht | cULus, NYC | 105a-f
| M QR Dry SSP (Plain Brl.) | VK172 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Br, Chr, Wht | cULus, NYC | 105a-f
| QR LO Dry SSP (Rec. Adj.) | VK181 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 105h-n
| QR LO Dry SSP (Std. Adj.) | VK177 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 105h-n
| QR LO Dry SSP (Plain Brl.) | VK173 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Large | 8 | 1" | Br, Chr, Wht | cULus, NYC | 105h-n
| QR LO Dry Fusible Link SSP (Rec. Adj.) | VK290 | Quick | 175 | 165° 205° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 105p-v
| QR LO Dry Fusible Link SSP (Std. Adj.) | VK286 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 105p-v
| QR LO Dry Fusible Link SSP (Plain Brl.) | VK282 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Large | 8 | 1" | Br, Chr | cULus, NYC | 105p-v
| QR LO Dry HSW (Rec. Adj.) | VK279 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 106s-z
| QR LO Dry HSW (Std. Adj.) | VK277 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 106s-z
| QR LO Dry HSW (Plain Brl.) | VK275 | Quick | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Large | 8 | 1" | Br, Chr, Wht | cULus, NYC | 106s-z
| QR LO Dry Fusible Link HSW (Rec. Adj.) | VK292 | Quick | 175 | 165° 205° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 107o-t
| QR LO Dry Fusible Link HSW (Std. Adj.) | VK288 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 107o-t
| QR LO Dry Fusible Link HSW (Plain Brl.) | VK284 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Large | 8 | 1" | Br, Chr | cULus, NYC | 107o-t
| QR Dry Concealed SSP | VK194 | Quick | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr, Wht, Iv, Blk | cULus, NYC | 104j-n
| HQR-2 SSP Institutional | VK410 | Quick | 175 | 165° 220° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Chr | cULus, NYC | 126a-d
| M QR ECOH ELO SSU | VK532 | Quick | 175 | 155° | 12' x 12' | 14' x 14' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 83a-f
| M QR EC ELO SSU (HC-1 and HC-2) | VK532 | Standard | 175 | 155° 175° 200° 286° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk | FM, NYC†† | 83a-f
| M ECOH ELO SSU | VK532 | Standard | 175 | 155° 175° 200° 286° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC | 83a-f
| QR ECOH ELO Fusible Element SSU | VK535 | Standard | 175 | 165° 205° | 14' x 14' | 14' x 14' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 83o-t
| ECOH ELO Fusible Element SSU | VK535 | Standard | 175 | 165° 205° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 83o-t
| QR EC ELO Fusible Element SSU (for HC-1 and HC-2) | VK535 | Standard | 175 | 165° 205° 280° | 12' x 12' | 16' x 16' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk | FM, NYC†† | 83o-t
| M ECOH ELO SSP | VK534 | Standard | 175 | 155° 175° 200° 286° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC | 83a-f
| ECOH ELO Fusible Element SSP | VK537 | Standard | 175 | 165° 205° | 16' x 16' | 20' x 20' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 83o-t
| M QR ECOH ELO SSP | VK534 | Quick | 175 | 155° | 12' x 12' | 14' x 14' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 83a-f
| QR ECOH ELO Fusible Element SSP | VK537 | Quick | 175 | 165° 205° | 14' x 14' | 14' x 14' | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 83o-t
| ECOH ELO Concealed Fusible Element SSP | VK538 | Standard | 175 | 165° | 12' x 12' | 20' x 20' | Extra Large | 11.2 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 89h-l
| QR ECOH ELO Concealed Fusible Element SSP | VK538 | Quick | 175 | 165° 205° | 12' x 12' | 20' x 20' | Extra Large | 11.2 | 3/4" | Chr, Wht, Iv, Blk | cULus, NYC†† | 89h-l
| ECOH SSU (K14.0) | VK570 | Standard | 175 | 155° 175° 200° 286° | 12' x 12' | 20' x 20' | N/A | 14 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC | 83h-m
| QR ECOH SSU (K14.0) | VK570 | Quick | 175 | 155° 175° 200° 286° | 12' x 12' | 14' x 14' | N/A | 14 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC | 83h-m
| ECOH SSP (K14.0) (Rec)* | VK572 | Standard | 175 | 155° 175° 200° 286° | 12' x 12' | 20' x 20' | N/A | 14 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC | 83h-m
| QR ECOH SSP (K14.0) (Rec)* | VK572 | Quick | 175 | 155° 175° 200° 286° | 12' x 12' | 14' x 14' | N/A | 14 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC | 83h-m
| QR EC SSP (K14.0) (for HC-1 and HC-2) | VK572 | Standard | 175 | 155° 175° 200° 286° | 12' x 12' | 20' x 20' | N/A | 14 | 3/4" | Br | FM, NYC†† | 83h-m
Light†, | M SSU | VK100 | Standard | 175 | 135° 155° 175° 200° 212° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC | 11q-v | 12a-f
Ordinary, | M SSU | VK145 | Standard | 175 | 135° 155° 175° 200° 212° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | FM, NYC†† | 11q-v | 12a-f
and Extra | M Stainless Steel SSU | VK130 | Standard | 175 | 155° 175° 200° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Stainless Steel, Wx Over Stainless Steel | cULus, FM, NYC | 15a-e
Hazard | M SSU | VK200 | Standard | 175 | 135° 155° 175° 200° 212° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC | 11q-v
| M SSU (for retrofit only) | VK200 | Standard | 175 | 135° 155° 175° 200° 212° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC | 11q-v
| M Stainless Steel SSP | VK132 | Standard | 175 | 155° 175° 200° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Stainless Steel, Wx Over Stainless Steel | cULus, FM, NYC | 15a-e
| M SSP (Rec)* | VK102 | Standard | 175 | 135° 155° 175° 200° 212° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC | 11a-h | 12a-f
| M SSP (Rec)* | VK202 | Standard | 175 | 135° 155° 175° 200° 212° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC | 11a-h
| M SSP (Rec)* (for retrofit only) | VK202 | Standard | 175 | 135° 155° 175° 200° 212° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC | 11a-h
Light†, | M Fusible Link SSP (Rec)* | VK110 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, Wx | cULus, FM, NYC | 18a-f | 18u-z
Ordinary, | M Fusible Link SSP (Rec)* | VK206 | Standard | 175 | 165° 220° 286° (FM 165° 286°) | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr, Wx | cULus, FM, NYC | 18a-f
and Extra | M Fusible Link SSP (Rec) (for retrofit only) | VK206 | Standard | 175 | 165° 220° 286° | Per NFPA | Per NFPA | Large | 8 | 1/2" | Br, Chr, Wx | cULus, NYC | 18a-f
Hazard | M Fusible Link SSU | VK108 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, Wx | cULus, FM, NYC | 18a-f | 18u-z
(continued) | M Fusible Link SSU | VK204 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr, Wht, Blk, Wx | cULus, FM, NYC | 18a-f
| M Fusible Link SSU (for retrofit only) | VK204 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 1/2" | Br, Chr, Wht, Blk, Wx | cULus, FM, NYC | 18a-f
| M Conventional | VK118 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br, Chr, Wht, Blk, BT, Wx | cULus, NYC | 11q-v
| M Conventional | VK120 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA | Per NFPA | Large | 8 | 3/4" | Br, Chr, Wht, Blk, BT, Wx | cULus, NYC | 11q-v
| SSU K=16.8 | VK580 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | N/A | 16.8 | 3/4" | Br | cULus, FM, NYC†† | 13a-d
| M ELO SSU | VK530 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC†† | 13e-i
| M ELO SSP (Rec) | VK536 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT, Wx | cULus, FM, NYC | 13e-i
| N-2 SSU Stainless Steel | VK130 | Standard | 175 | 155° 175° 200° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Stainless Steel, Wx | cULus, FM, NYC | 15a-e
| N-2 SSP Stainless Steel | VK132 | Standard | 175 | 155° 175° 200° 286° 360° 500° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Stainless Steel, Wx | cULus, FM, NYC | 15a-e
| Concealed SSP | VK102 | Standard | 175 | 155° 175° 200° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Chr, Wht, Iv, Blk | cULus, FM, NYC†† | 11j-o
| LO Concealed SSP | VK202 | Standard | 175 | 155° 175° 200° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Chr, Wht, Iv, Blk | cULus, FM, NYC†† | 11j-o
| B-2 EC Concealed Pendent (for retrofit only) | VK627 | Standard | 175 | 165° (220° No Approvals) | 20' x 20' | 20' x 20' | Large | 8 | 1/2" | BBR, Chr, AntBr, BrBr, BrChr, BrCpr, Wht, Iv, Blk | cULus, NYC†† | 87a-c
| M Dry Upright | VK160 | Standard | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Br, Chr, Wht | cULus, NYC | 101j-n
| M Dry SSP (Std. Adj.) | VK154 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1" | Br, Chr, Wht | cULus, FM, NYC | 101a-g
| M Dry SSP (Rec. Adj.) | VK158 | Standard | 175 | 155° 175° 200° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1" | Br, Chr, Wht | cULus, FM, NYC | 101a-g
| M Dry SSP (Plain Brl.) | VK150 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1" | Br, Chr, Wht | cULus, FM, NYC | 101a-g
| M LO Dry SSP (Std. Adj.) | VK163 | Standard | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 101o-t
| M LO Dry SSP (Rec. Adj.) | VK164 | Standard | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Large | 8 | 1" | Chr, Wht | cULus, NYC | 101o-t
| M LO Dry SSP (Plain Brl.) | VK166 | Standard | 175 | 155° 175° 200° 286° | Per NFPA | Per NFPA | Large | 8 | 1" | Br, Chr, Wht | cULus, NYC | 101o-t
| Dry Concealed SSP | VK190 | Standard | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 5.6 | 1" | Chr, Wht, Iv, Blk | cULus, NYC | 104a-f
| LO Dry Concealed SSP | VK192 | Standard | 175 | 155° 175° 200° | Per NFPA | Per NFPA | Standard | 8 | 1" | Chr, Wht, Iv, Blk | cULus, NYC†† | 104q-v
| A-2 High Challenge Large Drop | VK540 | Standard | 175 | 155° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br | cULus, FM, NYC | 113a-e
| A-2 High Challenge Large Drop (for retrofit only) | VK540 | Standard | 175 | 155° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 1/2" | Br | cULus, FM, NYC | 113a-e
Storage | M ELO SSU | VK530 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, BT, Wx | cULus, FM, NYC†† | 13e-i
| M ELO SSP | VK536 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, BT, Wx | cULus, FM, NYC | 13e-i
| M QR ELO SSU | VK531 | Quick | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 70h-k
| QR ELO Fusible Element SSU | VK533 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, NYC†† | 70w-z
| M QR ELO SSP | VK377 | Quick | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br, Chr, Wht, Blk, BT | cULus, FM, NYC | 70a-e
| SSU K=16.8 | VK580 | Standard | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | N/A | 16.8 | 3/4" | Br | cULus, FM, NYC | 13a-d
| SSP K=19.6 (CMSA) | VK592 | Standard | 175 | 160° 205° | UL, FM | UL, FM | N/A | 19.6 | 1" | Br | UL, FM, NYC†† | 114l-s
| A-2 High Challenge Large Drop | VK540 | Standard | 175 | 155° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 3/4" | Br | cULus, FM, NYC | 113a-e
| A-2 High Challenge Large Drop (for retrofit only) | VK540 | Standard | 175 | 155° 200° 286° | Per NFPA, FM | Per NFPA, FM | Extra Large | 11.2 | 1/2" | Br | cULus, FM, NYC | 113a-e
| A-4 ESFR Upright | VK520 | Fast | 175 | 165° 205° | Per NFPA, FM | Per NFPA, FM | N/A | 14 | 3/4" | Br | FM, NYC | 121a-e
| S-1 ESFR Pendent | VK500 | Fast | 175 | 165° 205° | Per NFPA, FM | Per NFPA, FM | N/A | 14 | 3/4" | Br | cULus, FM, NYC | 120a-f
| ESFR Pendent | VK502 | Fast | 175 | 165° | Per NFPA, FM | Per NFPA, FM | N/A | 14 | 1-1/2", 2" | Br | cULus, FM | 122j-q
| ESFR Pendent | VK503 | Fast | 175 | 165° 205° | Per NFPA, FM | Per NFPA, FM | N/A | 16.8 | 3/4" | Br | cULus, FM, NYC | 123a-f
| ESFR Pendent | VK504 | Fast | 175 | 165° | Per NFPA | Per NFPA | N/A | 16.8 | 1-1/2" | Br | cULus | 129a-h
| ESFR Pendent | VK506 | Fast | 175 | 165° 205° | Per NFPA, FM | Per NFPA, FM | N/A | 22.4 | 1" | Br | cULus, FM | 128a-f
| ESFR Pendent | VK510 | Fast | 175 | 165° 205° | Per NFPA, FM | Per NFPA, FM | N/A | 25.2 | 1" | Br | cULus (Specific App), FM, NYC†† | 124a-f
Intermediate | M SSU Intermediate Level/Rack Storage | VK100 | Standard | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | FM, NYC†† | 130e-h
Level In-Rack | M SSU Intermediate Level/Rack Storage | VK145 | Standard | 175 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br | FM, NYC†† | 130e-h
Storage | M SSU Intermediate Level/Rack Storage | VK200 | Standard | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br | FM, NYC†† | 130e-h
| M SSU Intermediate Level/Rack Storage | VK550 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | cULus, FM, NYC†† | 131a-e
| M SSU Intermediate Level/Rack Storage | VK560 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br | cULus, FM, NYC†† | 131a-e
| M SSU Intermediate Level/Rack Storage (for retrofit only) | VK560 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 1/2" | Br | cULus, FM, NYC†† | 131a-e
| M SSP Intermediate Level/Rack Storage | VK202 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br | cULus, FM, NYC†† | 130e-h | 131a-e
| M SSP Intermediate Level/Rack Storage | VK102 | Standard | 175 | 135° 155° 175° 200° 286° 360° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | cULus, FM, NYC†† | 130e-h | 131a-e
| M Link SSU Intermediate Level/Rack Storage | VK108 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | FM, NYC | 130e-h
| M Link SSU Intermediate Level/Rack Storage | VK204 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br | FM, NYC | 130e-h
| M Link SSU Intermediate Level/Rack Storage | VK552 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | cULus, FM, NYC†† | 131a-e
| M Link SSU Intermediate Level/Rack Storage | VK562 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br | cULus, FM, NYC†† | 131a-e
| M Link SSP Intermediate Level/Rack Storage | VK110 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | cULus, FM, NYC | 130e-h | 131a-e
| M Link SSP Intermediate Level/Rack Storage | VK206 | Standard | 175 | 165° 220° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br | cULus, FM, NYC | 130e-h | 131a-e
| M QR SSU Intermediate Level/Rack Storage | VK300 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr | FM, NYC | 130e-h
| M QR SSU Intermediate Level/Rack Storage | VK350 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr | FM, NYC | 130e-h
| M QR SSP Intermediate Level/Rack Storage | VK302 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | cULus, FM, NYC†† | 130e-h | 131a-e
| M QR SSU Intermediate Level/Rack Storage | VK566 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br | cULus, FM, NYC†† | 131a-e
| M QR SSP Intermediate Level/Rack Storage | VK302 | Quick | 175 | 135° 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br, Chr | cULus, FM, NYC | 130e-h | 131a-e
| M QR HP SSP Intermediate Level/Rack Storage | VK317 | Quick | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br | cULus, NYC†† | 131a-e
| M QR HP SSU Intermediate Level/Rack Storage | VK558 | Quick | 250 | 135° 155° 175° 200° 286° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br | cULus, NYC†† | 131a-e
| QR Fusible Element SSU Intermediate Level/Rack Storage | VK551 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br | cULus, NYC†† | 131a-e
| QR Fusible Element SSU Intermediate Level/Rack Storage | VK557 | Quick | 175 | 165° 205° 280° | Per NFPA, FM | Per NFPA, FM | Standard | 5.6 | 1/2" | Br | cULus, FM, NYC†† | 131a-e
| QR Fusible Element SSU Intermediate Level/Rack Storage | VK567 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Large | 8 | 3/4" | Br | cULus, FM, NYC†† | 131a-e
| M QR SSP Intermediate Level/Rack Storage | VK352 | Quick | 175 | 155° 175° 200° 286° | Per NFPA, FM | Per NFPA, FM | Large | 8 | 3/4" | Br, Chr | cULus, FM, NYC | 130e-h | 131a-e
| QR Fusible Element SSP Intermediate Level/Rack Storage | VK303 | Quick | 175 | 165° 205° 280° | Per NFPA | Per NFPA | Standard | 5.6 | 1/2" | Br | cULus, NYC†† | 131a-e
Nozzles | 1/4" C-1 Window Sprinkler | VK790 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" | 1.5 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 11-14
| 5/16" C-1 Window Sprinkler | VK791 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 5/16" | 2.1 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 11-14
| 3/8" C-1 Window Sprinkler | VK792 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 3/8" | 3 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 11-14
| 7/16" C-1 Window Sprinkler | VK793 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 7/16" | 4.3 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 11-14
| 1/2" C-1 Window Sprinkler | VK794 | Open | N/A | OPEN | Per NFPA | Per NFPA | 1/2" | 5.8 | 1/2" | Br, Electroless Nickel | cULus, NYC | SN 11-14
| 5/8" C-1 Window Sprinkler | VK795 | Open | N/A | OPEN | Per NFPA | Per NFPA | 5/8" | 7.3 | 3/4" | Br, Electroless Nickel | cULus, NYC | SN 11-14
| 3/4" C-1 Window Sprinkler | VK796 | Open | N/A | OPEN | Per NFPA | Per NFPA | 3/4" | 8.1 | 3/4" | Br, Electroless Nickel | cULus, NYC | SN 11-14
| 30° A-2 Spray Nozzle | VK740 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 1.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 60° A-2 Spray Nozzle | VK741 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 1.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 90° A-2 Spray Nozzle | VK742 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 1.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 120° A-2 Spray Nozzle | VK743 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 1.4 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 140° A-2 Spray Nozzle | VK744 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 1.4 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 30° A-2X Spray Nozzle | VK750 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 60° A-2X Spray Nozzle | VK751 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 90° A-2X Spray Nozzle | VK752 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 120° A-2X Spray Nozzle | VK753 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 2.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 140° A-2X Spray Nozzle | VK754 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 1/4" Dia | 2.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 30° B-2 Spray Nozzle | VK760 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 11/32" Dia | 2.8 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 60° B-2 Spray Nozzle | VK761 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 11/32" Dia | 2.8 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 90° B-2 Spray Nozzle | VK762 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 11/32" Dia | 2.8 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 120° B-2 Spray Nozzle | VK763 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 11/32" Dia | 3.3 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
Nozzles | 140° B-2 Spray Nozzle | VK764 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 11/32" Dia | 3.3 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
(continued) | 30° C-2 Spray Nozzle | VK770 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 3/8" Dia | 3.4 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 60° C-2 Spray Nozzle | VK771 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 3/8" Dia | 3.4 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 90° C-2 Spray Nozzle | VK772 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 3/8" Dia | 3.8 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 120° C-2 Spray Nozzle | VK773 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 3/8" Dia | 3.9 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 140° C-2 Spray Nozzle | VK774 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 3/8" Dia | 3.9 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 30° D-2 Spray Nozzle | VK780 | Open | N/A | OPEN | Per NFPA | Per NFPA | 7/16" Dia | 4.7 | 1/2" | Br, Electroless Nickel | cULus, NYC | SN 20-32
| 60° D-2 Spray Nozzle | VK781 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 7/16" Dia | 4.7 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 90° D-2 Spray Nozzle | VK782 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 7/16" Dia | 5 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 120° D-2 Spray Nozzle | VK783 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 7/16" Dia | 5.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 140° D-2 Spray Nozzle | VK784 | Open | N/A | OPEN | Per NFPA, FM | Per NFPA, FM | 7/16" Dia | 5.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 20-32
| 65° E Spray Nozzle | VK810 | Open | 175 | OPEN | Per NFPA, FM | Per NFPA, FM | N/A | 1.2-7.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 32a-i
| 80° E Spray Nozzle | VK811 | Open | 175 | OPEN | Per NFPA, FM | Per NFPA, FM | N/A | 1.2-7.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 32a-i
| 95° E Spray Nozzle | VK812 | Open | 175 | OPEN | Per NFPA, FM | Per NFPA, FM | N/A | 1.2-7.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 32a-i
| 110° E Spray Nozzle | VK813 | Open | 175 | OPEN | Per NFPA, FM | Per NFPA, FM | N/A | 1.2-7.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 32a-i
| 125° E Spray Nozzle | VK814 | Open | 175 | OPEN | Per NFPA, FM | Per NFPA, FM | N/A | 1.2-7.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 32a-i
| 140° E Spray Nozzle | VK815 | Open | 175 | OPEN | Per NFPA, FM | Per NFPA, FM | N/A | 1.2-7.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 32a-i
| 160° E Spray Nozzle | VK816 | Open | 175 | OPEN | Per NFPA, FM | Per NFPA, FM | N/A | 1.2-7.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 32a-i
| 180° E Spray Nozzle | VK817 | Open | 175 | OPEN | Per NFPA, FM | Per NFPA, FM | N/A | 1.2-7.2 | 1/2" | Br, Electroless Nickel | cULus, FM, NYC | SN 32a-i
* Check current technical data pages for specific listings and approvals. cULus indicates Listed by Underwriters Laboratories Inc. for use in the U.S. and Canada. **Check current technical data pages for available custom painting and corrosion resistant finishes.
† Effective starting with the 1996 edition of NFPA 13, quick response type sprinklers are required to be used in all Light Hazard Occupancies, with exceptions for existing systems that have standard response sprinklers.
††Meets New York City requirements, effective July 1, 2008.
(Rec), (Rec*) Indicates sprinklers that are available as recessed models. Check current technical data pages for listings and approvals as they may vary with temperature rating, spacings, approval agencies, etc.
Finishes: Br = Brass, BBR = Bright Brass, Chr = Chrome, AntBr = Antique Brass, BrBr = Brushed Brass, BrChr = Brushed Chrome, BrCpr = Brushed Copper, Wht = White, Iv = Ivory, Blk = Black, BT = Black Teflon, Wx = Wax Coated